## Slide 1
A $12 million battery. A $57 million project.
Hyde Park BESS (Project 21334): where the cost of a utility-owned, distribution-connected battery storage station actually sits, and how it compares to industry benchmarks
Cost Estimating Center of Excellence | Estimate basis: ESF Total Rev 3, 24 Sep 2026 | 29 Sep 2026
Internal. Contains vendor-confidential pricing.
Notes: Open on the promise, not a joke. The one sentence the audience should be able to repeat afterwards: the battery is 21 percent of the project, and the other 79 percent is what it takes to put a battery on a landfill in Boston and connect it to four feeders safely.

## Slide 2
THE PROMISE
By the end of this deck you can answer one question in one breath
EstimatingCoE | Eversource Energy | Stewards of Affordability
2
“Why is a $12 million battery a $57 million project?” Because the battery is the only part a vendor prices. The station, the site, the feeder protection, the siting case, the risk and the cost of money are ours.
$12.1M
Vendor fixed-price contract
Nomad cover agreement, 10 Mar 2026. 12 Voyager LFP units, PCS, BMS, fire protection, 10-yr warranty. $605/kWh, $1,211/kW.
$57.2M
Project 21334 approval level
ESF Total Rev 3. Station 360 $50.0M plus Station 496 protection $7.3M. $2,862/kWh, $5,725/kW. Conceptual, -25%/+50%.
21%
Battery share of the total
Add the D-Line circuit extension (24211, $4.8M conceptual) and the share drops to 20%. Four dollars of every five are not the battery.
What this deck contributes: a line-by-line extraction of the Rev 3 estimate into thirteen cost layers, unit costs at every boundary a benchmark could be quoted at, the cost history from the 2021 IFR to today, and the reconciliations that must close before full funding.
Notes: Three numbers. Vendor contract, approval level, share. Everything after this slide is proof.

## Slide 3
TWO FRAMINGS OF THE SAME PROJECT
What a vendor quote contains, and what it leaves for the utility
EstimatingCoE | Eversource Energy | Stewards of Affordability
3
Inside the $12.1M Nomad price
▪ 12 containerized LFP units, 10 MW / 20 MWh, 12 MVA
▪ Inverters (PCS), BMS, HVAC, fire detection and suppression inside the container
▪ Spares $125K, shipping $90K, remote support $210K
▪ 10-year warranty; years 3-7 extension $798K
▪ Field assembly supervision, commissioning, training: $246K
▪ Fixed until Final Acceptance; LDs capped at 10%
Outside it: $45.1M, 79% of the project
▪ Station 360, $3.8M direct: four 15 kV breaker skids, GSUs, SSVT, metering, cable, duct bank, ground grid
▪ Site, $2.7M direct: a 200 ft x 200 ft platform on a closed landfill, access road, retaining wall
▪ Station 496, $7.3M: 20 relays, transfer trip, RTU work so four feeders can accept 2.5 MW each
▪ Owner scope, $10.1M: install labor, GSUs, EMS, testing, engineering, Article 80 siting, outreach, PM, taxes
▪ Station 360 risk, contingency, indirects, AFUDC, $20.3M: 35% of the total (Station 496 carries its own inside its $7.3M)
Notes: The vendor is not wrong. Their number is a real number for what they sell. It is simply not the project.

## Slide 4
COST LAYER EXTRACTION, ESF TOTAL REV 3 (DIRECTS, $M)
Thirteen layers between the battery contract and the approval level
EstimatingCoE | Eversource Energy | Stewards of Affordability
4
Chart: 
| A Battery contract $13.0M | B Battery install $1.7M | C Battery BOP (GSU, EMS) $1.9M | D Sta 360 switching $3.8M | E Site & civil $2.7M | F Sta 496 protection $7.3M | G Testing $1.3M | H Owner soft costs $4.4M | I Taxes, CWIP, BAR $0.8M | J Risk $5.3M | K Contingency $2.3M | L Indirects $8.1M | M AFUDC $4.7M
base | 0 | 12.99 | 14.72 | 16.66 | 20.5 | 23.19 | 30.45 | 31.71 | 36.13 | 36.92 | 42.22 | 44.5 | 52.57
Layer | 12.99 | 1.73 | 1.93 | 3.85 | 2.69 | 7.25 | 1.26 | 4.42 | 0.79 | 5.3 | 2.28 | 8.06 | 4.68
Gold = battery contract as carried in Rev 3 ($12.1M contract plus $1.1M escalation on the unpaid balance; see slide 12). Teal = station, site and feeder protection. Burgundy = risk, contingency, indirects, AFUDC. Total $57.2M.
Notes: Read left to right. The battery contract is the first bar. Everything to its right is the utility's project.

## Slide 5
LOADED VIEW: EVERY LAYER CARRIES ITS SHARE OF THE LOADERS (FACTOR 1.685 ON STATION 360 DIRECTS)
Where the $57.2M sits when risk, contingency, indirects and AFUDC are spread
EstimatingCoE | Eversource Energy | Stewards of Affordability
5
Layer | Direct | Loaded | Share
Battery supply contract (Nomad) | $13.0M | $21.9M | 38%
Battery installation & integration (owner scope) | $1.7M | $2.9M | 5%
Battery balance-of-plant (GSUs, EMS/comms, aux power) | $1.9M | $3.3M | 6%
Station 360 13.8 kV switching & interconnection facilities | $3.8M | $6.5M | 11%
Site development & civil (former landfill site) | $2.7M | $4.5M | 8%
Station 496 feeder protection upgrades (interconnection) | $7.3M | $7.3M | 13%
Testing & commissioning | $1.3M | $2.1M | 4%
Owner soft costs (engineering, siting, environmental, outreach, PM, land) | $4.4M | $7.4M | 13%
Taxes, CWIP, builders-risk insurance | $0.8M | $1.3M | 2%
Total, project 21334 (directs incl. $20.3M of loaders J-M) | $57.2M | $57.2M | 100%
Battery-related layers A+B+C loaded: $28.1M (49%). Station, site and feeder interconnection D+E+F loaded: $18.3M (32%). Owner soft costs, testing and taxes: $10.9M.
Notes: The loaded view is the honest comparison basis. When someone quotes an all-in industry $/kWh, it already carries developer overhead and financing; ours carries indirects and AFUDC.

## Slide 6
UNIT COST AT EACH BOUNDARY, 20 MWH / 10 MW
The same project is $605/kWh or $2,862/kWh depending on where you draw the line
EstimatingCoE | Eversource Energy | Stewards of Affordability
6
Chart: 
| Vendor contract | Battery as carried (contract + escalation) | Battery installed (A+B+C) | Station complete, direct (no loaders) | Station 360 approval level | Project 21334 (Sta 360 + 496) | All-in incl. D-Line memo
$/kWh | 605 | 650 | 833 | 1483 | 2500 | 2862 | 3102
Boundary | $/kW | $/kWh | x
Vendor contract | $1,211 | $605 | 1.0x
Battery installed | $1,666 | $833 | 1.4x
Sta 360 approval | $4,999 | $2,500 | 4.1x
Project 21334 | $5,725 | $2,862 | 4.7x
Incl. D-Line | $6,204 | $3,102 | 5.1x
A benchmark is only meaningful against the row that matches its definition. Pack and DC-block prices belong beside the top bar; NREL and EIA installed costs beside 'battery installed' or 'station complete'; nothing published includes a utility's own indirects and AFUDC.
Notes: This is the slide that ends the argument. The multiple between the vendor line and the approval level is 4.7x, and each step between them is a named scope.

## Slide 7
INDUSTRY BENCHMARKS VS HYDE PARK BOUNDARIES ($/KWH, NOMINAL)
The battery is at market; the project is above it, for reasons the benchmarks exclude
EstimatingCoE | Eversource Energy | Stewards of Affordability
7
Chart: 
| BNEF pack, stationary (2025) | Anza distribution-scale AC, delivered (Q1 2026) | BNEF US turnkey system (2025) | NREL all-in, 4-h 60 MW (2024) | EIA/S&L overnight, 4-h 150 MW (2023$) | LBNL empirical all-in, 2024 hybrids | HECO Waena 40 MW/160 MWh, utility-owned | NV Energy Reid Gardner 2-h, utility-owned | Eversource Provincetown 1.5-h, final (2022) | Hyde Park: Nomad equipment only | Hyde Park: vendor contract | Hyde Park: battery installed (A+B+C) | Hyde Park: station complete, direct | Hyde Park: project 21334 approval level
$/kWh | 70 | 203 | 219 | 334 | 436 | 458 | 513 | 584 | 1289 | 532 | 605 | 833 | 1483 | 2862
▪ Battery at market. Nomad's $532/kWh equipment price sits between BNEF's US turnkey ($219, 4-h, 100 MW class) and the disclosed utility-owned projects ($513-584). For a 12-unit, 2-h, FEOC-era order in New England that is a fair price.
▪ Installed battery (A+B+C) at $833/kWh is above every national all-in index because those indices are four-hour and 60-150 MW. NREL's own cost structure (pack $/kWh x hours + BOS $/kW) puts a 2-h system at roughly 1.3-1.5x the 4-h $/kWh.
▪ The project at $2,862/kWh is not a battery benchmark at all. It carries a switching station, feeder protection at Station 496, a landfill platform, Article 80 siting, indirects and AFUDC. The closest published analogue is Provincetown at $1,289/kWh (2022 dollars, no separate station, existing site).
▪ No published index includes a utility's indirects or AFUDC. Strip J-M and Hyde Park is $1,483/kWh direct; strip the station and site layers D and E as well and it is $1,156/kWh.
Notes: Benchmarks were retrieved from search-index excerpts of the primary sources because the sandbox proxy blocked direct downloads; each row carries a confidence tag and a URL. Before this slide is used externally, pull the NREL ATB 2025 workbook 2-h values, the Lazard v11 capex input table and the PNNL 10 MW rows directly.

## Slide 8
WHY A SMALL URBAN UTILITY-OWNED PROJECT SITS ABOVE THE INDEX
Six things about Hyde Park that a 100 MW greenfield benchmark never has to pay for
EstimatingCoE | Eversource Energy | Stewards of Affordability
8
Size. 10 MW / 20 MWh. A switching station, a siting case and a commissioning team cost about the same at 10 MW as at 100 MW; per kWh they are ten times heavier.
Duration. Two hours. Fixed $/kW items (PCS, breakers, GSUs, interconnection) are spread over half the MWh of a four-hour benchmark.
Site. A closed construction-debris landfill in Boston: DEP post-closure use permit, cap protection, 36 borings, imported platform fill, 14 ft retaining wall, unknown obstructions ($450K risk).
Interconnection. Four feeder tie-ins at 13.8 kV, each with its own breaker skid, plus relay replacement and transfer trip at Station 496 ($7.3M) and a 5,465 ft circuit extension (24211).
Siting and outreach. Article 80 Small Project Review, Zoning Board of Appeal, outside counsel, an EJ community, a neighborhood concerned about open land and views: $1.5M plus $0.5M in the risk register.
Utility accounting. Corporate indirects ($10.0M) and AFUDC over a seven-year development window ($5.0M) are real costs to customers that a developer's turnkey price never shows.
Notes: None of these six is optional and none of them is the battery.

## Slide 9
COST HISTORY, 2021 TO 2026 (APPROVAL-LEVEL ESTIMATES AND VENDOR PRICE POINTS)
Five years, five in-service dates, and an estimate that moved from $44M to $57M
EstimatingCoE | Eversource Energy | Stewards of Affordability
9
Chart: 
| Jun 2021 IFR | Jul 2023 Vendor indicative (Company 3, turnkey) | Dec 2023 E-23-373 conceptual | Feb 2024 SSF incl. D-Line | Mar 2026 Nomad contract | Aug 2026 Rev 0 | Sep 2026 Rev 2 | Sep 2026 Rev 3
$M | 0.2 | 18.2 | 43.9 | 49.2 | 12.1 | 47.2 | 63.6 | 57.2
In-service date drift
As of | Planned ISD
Jun 2021 | Q3 2025
Dec 2023 | Apr 2027
Feb 2024 | Sep 2027
Jan 2026 | Aug 2028
Jun 2026 | Dec 2028
Gold bars are vendor prices for the battery scope only. Navy bars are full project estimates. The battery price fell from $18.2M turnkey-indicative (2023, incl. civil) to $12.1M contracted (2026); the project rose $13.3M in the same window. The 2023 conceptual carried a placeholder that was never re-based until August 2026.
Notes: The story is not that batteries got expensive. The battery got cheaper. The project got more real.

## Slide 10
PAF CATEGORY COMPARISON, PROJECT 21334 ($M)
What changed between the December 2023 conceptual and Rev 3: $43.9M to $57.2M
EstimatingCoE | Eversource Energy | Stewards of Affordability
10
Chart: 
| Materials | Construction | Testing | Engineering | Siting + Env + Outreach | PMT | Other | Risks | Contingency | Indirects | AFUDC
E-23-373 (Dec 2023) | 13.76 | 6.92 | 1.06 | 0.79 | 0.84 | 1.04 | 0.93 | 3.95 | 1.81 | 9.52 | 3.3
Rev 3 (Sep 2026) | 16.68 | 8.05 | 3.08 | 0.96 | 1.91 | 1.89 | 0.99 | 6.07 | 2.62 | 9.99 | 5.01
Largest movements
Category | Delta
Materials | +$2.9M
Risks | +$2.1M
Testing | +$2.0M
AFUDC | +$1.7M
Construction | +$1.1M
Siting + Env + Outreach | +$1.1M
PMT | +$0.9M
Materials: contracted battery replaces 2023 indicative pricing, plus breaker skids and GSUs. Testing and siting: Station 496 scope and Article 80 were not in E-23-373. AFUDC: a 20-month later ISD on a larger base.
Notes: Materials up 2.9, testing up 2.0, siting up 1.4, risk up 2.1, AFUDC up 1.7. Those five are 10.1 of the 13.3.

## Slide 11
REVISION WALK, 26 AUG TO 24 SEP 2026
Four revisions in five weeks: how the September estimate settled at $57.2M
EstimatingCoE | Eversource Energy | Stewards of Affordability
11
Chart: 
| Rev 0 26 Aug | Battery to project team value | Rev 1 1 Sep | Battery to contract + relays + eng | Rev 2 10 Sep | Relays -1.5, SSVT, eng re-base | Rev 3 24 Sep
base | 0 | 47.2 | 0 | 51.9 | 0 | 57.2 | 0
val | 47.2 | 4.7 | 51.9 | 11.8 | 63.6 | 6.4 | 57.2
▪ Rev 0 carried the battery at about $6M from the 2023 indicative sheet. The PM: 'we know the BESS system itself is 12.'
▪ Rev 2 reset it to the cover agreement, escalated to $13.1M, and carried $1.5M of 'relays for batteries' from a 2023 bidder that priced its own switchgear.
▪ Rev 3 removed the relays (P&C Engineering: included in the $300K Siemens skid), cut three SSVTs to one, and re-based engineering to $501K to go plus actuals.
▪ Net: +$10.0M from Rev 0, of which $7.0M is the battery line catching up to the contract.
Notes: This walk is in the email record. It matters because the full-funding placeholder of $43.9M was never touched between December 2023 and August 2026.

## Slide 12
BATTERY SCOPE PRICE POINTS ($/KWH AT 20 MWH)
The battery itself: a $9.6M-$18.2M indicative spread in 2023, a $12.1M fixed price in 2026
EstimatingCoE | Eversource Energy | Stewards of Affordability
12
Chart: 
| Company 1 | Company 2 (Opt 1) | Company 2 (Opt 2) | Company 3 | Company 4 | Company 5 | Nomad contract Mar 2026
$/kWh | 578 | 527 | 479 | 911 | 574 | 696 | 605
▪ July 2023, five bidders, 10 MW / 20 MWh: $9.6M to $18.2M. Every bidder excluded interconnection, permits beyond local, below-grade risk, sound walls or spares.
▪ Company 3 ($18.2M, burgundy) became the E-23-373 basis because it alone priced turnkey civil ($4.56M) and installation.
▪ March 2026 contract, $12.1M (gold): supply only, with supervision. Civil, install, GSUs, station and interconnection moved to Eversource scope.
▪ Equipment-only inside the contract: $10.64M, $532/kWh, in line with published 2025-26 turnkey system indices (slide 7).
▪ Rev 3 adds $1.13M of escalation to a price the contract fixes until Final Acceptance.
Notes: The lesson from 2023: a low bid with exclusions is not a low project. The lesson from 2026: the vendor price is defensible. It is the boundary that moved.

## Slide 13
WHAT IT TAKES TO PUT 10 MW ON FOUR 13.8 KV FEEDERS
Station and interconnection facilities: $18.3M loaded, and none of it in a vendor quote
EstimatingCoE | Eversource Energy | Stewards of Affordability
13
Chart: 
| Station 360 switching facilities (D) | Site development on landfill (E) | Station 496 protection (F) | D-Line 24211 (memo)
Loaded $M | 6.48 | 4.53 | 7.25 | 4.79
$18.3M
Loaded, in 21334
32% of the approval level
$23.1M
Incl. D-Line memo
37% of the all-in view
▪ Four Siemens SDV7 breaker skids at $300K each (relays, PTs, DC battery, cabinet on the skid), disconnects, four metering transclosures, station service, riser poles, 15 kV cable and 1,240 ft of duct bank.
▪ Station 496: 20 SEL relays replacing SEL-551 and REF610 units on four feeders, RTU and RTAC points, transfer trip over dark fiber; $1.8M of that is testing.
▪ Site: 2.5 acres cleared, 760 ft road, 2,520 CY cut, imported fill, 14 ft retaining wall, ground grid, fence, lighting; Haugland's platform take-off is larger than ours and is unreconciled.
▪ D-Line (24211): 5,465 ft feeder extension, three manholes, 16,395 ft of 3-700 cable; $4.8M is a 2023 conceptual figure.
Notes: These are the facilities that make a battery a grid asset. A vendor's job ends at the container terminals.

## Slide 14
LOADERS ON PROJECT 21334
Risk, contingency, indirects and AFUDC are 41% of the approval level
EstimatingCoE | Eversource Energy | Stewards of Affordability
14
Chart: 
| Risk register | Contingency | Indirects / overheads | AFUDC
$M | 6.07 | 2.62 | 9.99 | 5.01
Station 360 risk item | $K
Material cost, tariffs | 1,000
Design / scope change orders | 800
Labor cost, shortage, overtime | 800
Unforeseen UG obstructions (landfill) | 450
Environmental (DEP, landfill closure docs) | 300
Soil contamination remediation | 300
Station and P&C engineering changes | 600
Weather, siting delay, outreach, BAR deductibles | 1,050
Risk plus contingency is 17.9% of the approval level before loaders, inside the 15-18% lead-review guidance. Indirects at 17.4% and AFUDC at 8.8% follow the EMA station template on a spend curve that runs from July 2021 to December 2028. Haugland's Attachment 4-F carries overlapping exposures (geotech $0.6M-$3.5M, fault-study equipment change $0.25M-$1.8M) that have not been reconciled with this register.
Notes: AFUDC is the cost of a seven-year development window. Every month of siting delay adds to it.

## Slide 15
RECONCILIATIONS AND DECISIONS, WITH THE DOLLARS AT STAKE
What must close before this number goes to EPAC as full funding
EstimatingCoE | Eversource Energy | Stewards of Affordability
15
Item | Type | Dollars at stake | Owner
Reconcile Haugland Class 3 base ($19.2M, its scope) to Rev 3 layers B+D+E ($8.3M direct) | Scope boundary | Unknown until mapped | Cost Estimating + PM + HEG
Confirm four written design-basis items (retaining wall, detention basin, duct bank, GSU count) | Design confirmation | $1.47M HEG deduct ceiling | Substation Engineering
Escalation on the fixed-price battery balance | Decision | $1.13M | PM / Cost Estimating
Geotechnical investigation before IFC (platform depth, bearing) | Study | $0.38M deduct or $0.6M-$3.5M exposure | Civil Engineering
NFPA 855 hazard mitigation analysis before civil freeze (footprint 36,100 vs 17,040 SF) | Study | $0.58M deduct; containment $0.10M | Capital Projects Eng.
Re-base D-Line 24211 (2023 conceptual $4.8M; HEG take-off larger) | Estimate | Unknown | Distribution Engineering
Battery installation labor: replace 25%-of-16,801 mh with a crew build-up | Estimate | +/- $0.5M | Cost Estimating + Nomad
Present full funding as Planning grade (-25/+25%) once the above close | Classification | Range narrows from -$14M/+$29M | Cost Estimating
Haugland's own roll-up: $2.9M achievable deduct ceiling against its base, $0.15M to capture, plus $1.5M of avoided cost outside the base. Ceiling, not forecast.
Notes: Every item has an owner and a dollar figure. That is what makes it a plan rather than a worry list.

## Slide 16
CONTRIBUTIONS
A $12 million battery is a $57 million project, and now every dollar between them has a name
▪ Cost layer extraction. 292 Rev 3 line items in thirteen layers, reconciled to the penny. Direct shares: battery contract 23%, battery install and balance of plant 6%, station and interconnection 24%, owner scope 11%, Station 360 loaders 35%.
▪ Unit costs at every boundary. $605/kWh vendor, $833 installed, $2,500 Station 360, $2,862 project, $3,102 all-in. Benchmarks compared against the row that matches their definition.
▪ Cost history. 2021 IFR to Rev 3, with the ISD drift and the five-week September walk documented from the ESF revisions and email record.
▪ Open-item register. Eight reconciliations with owners and dollars, led by the Haugland Class 3 reconciliation and the $1.13M escalation decision.
Decisions requested
▪ Adopt the layered view as the standard way this project is presented internally and to regulators: battery, station, interconnection, owner scope, loaders.
▪ Direct the Haugland-to-Rev 3 reconciliation before the full-funding PAF is drafted.
▪ Decide the escalation treatment on the fixed-price battery balance.
▪ Fund the geotechnical investigation and the NFPA 855 hazard mitigation analysis now; both gate $1M of deducts and $3.5M of exposure.
▪ Retire the $43.9M placeholder in the PAF narrative.
EstimatingCoE | Eversource Energy | Stewards of Affordability
Notes: Mirror the open. Leave this slide up for questions. Do not add a Questions slide.