## README
Hyde Park BESS (Project 21334 / 24211) - Cost Analysis Workbook
Purpose | Traceable data source behind the Cost Analysis deck, Basis of Estimate and all-in cost whitepaper. Every number on a slide ties to a cell here.
Prepared | Eversource Cost Estimating CoE, 29 Sep 2026. Source of record: ESF - Hyde Park BESS Total Rev 3.xlsm (24 Sep 2026), Item and Overview tabs.
Convention | Blue font = input value keyed from a source document (editable). Black = formula. Navy header = section. Gold fill = headline metric.
Tab: Layers | Rev 3 line items rolled into 13 cost layers (A-M). Directs are as-estimated; the 'Loaded' column spreads Station 360 risk, contingency, indirects and AFUDC pro rata over direct layers so each layer carries its full share of the approval-level total.
Tab: Unit Costs | $/kW and $/kWh at each boundary: vendor contract only, battery system installed, station complete, all-in approval level, and all-in including the D-Line interconnection (24211).
Tab: Timeline | Every funding action, estimate and vendor price point from the 2021 IFR to Rev 3, with basis and in-service date drift.
Tab: Sept 2026 Walk | Rev 0 -> Rev 1 -> Rev 2 -> Rev 3 variance walk from the ESF revisions and the 9/1-9/23/2026 email record.
Tab: Benchmarks | Published industry benchmarks with metric definition, dollar year and duration. Source quality tier: green = primary, yellow = secondary.
Tab: 2023 Indicative | July 2023 five-bidder indicative pricing (Site Two = Hyde Park 10 MW/20 MWh) and what each excluded.
Tab: Line Items | All 292 Rev 3 line items with the layer assignment used for the roll-up. Change a layer letter in column K and the Layers tab recalculates.
Vintage / escalation | Rev 3 carries $2,948,100 of escalation (ESF Overview). Battery line escalated at 3%/yr to 2027-28 delivery even though the Nomad price is fixed until Final Acceptance; see BOE section 'Escalation'.
Accuracy | Rev 3 is classed Conceptual (-25% / +50%) on the ESF. Sta 360 preliminary engineering is in progress (Sep 2026); IFC expected Aug 2027.
Tab: Public Projects | 44 public project costs compiled 29 Sep 2026 (26 used in the regression; exclusions and reasons in column N). $/kWh, $/kW and duration are formulas.
Tab: Statistics | Reference-class, regression and Monte Carlo results as values, with the model parameters. See the Statistical Benchmarking Memo for method and limits.
Cost Curve | Industry installed-cost series 2015-2035 as published (EIA, BNEF, NREL), Hyde Park points, the 2-h / 10 MW adjustment, the escalation carried in Rev 3 and the common-dollar comparison (deck slides 10-11). Added 2 Oct 2026.
2026$ Adjustment | Dollar-year adjustment of the 13 reference-class comparables to 2026 under three battery indices (selector in B6), battery-share and escalation inputs, medians and Hyde Park percentiles; New York distribution-scale cohort (NineDot, Elevate, Soltage, NYSERDA averages, Con Edison interconnection). Deck slides 12-13. Added 2 Oct 2026.

## Layers
Cost layers - ESF Total Rev 3 (24 Sep 2026), Project 21334 (Sta 360 + Sta 496)
Directs by layer are SUMIFS over the Line Items tab. Loaded = Station 360 direct layers x load factor (risk + contingency + indirects + AFUDC spread pro rata); Station 496 is carried whole as an interconnection cost.
Layer | Direct ($) | % of total | Loaded ($) | % of loaded | Cumulative loaded ($) | What it is
A. Battery supply contract (Nomad) | 12991103.8259 | 22.69% | 21893672.0362 | 38.24% | 21893672.0362 | Nomad fixed-price supply contract $12,106,850 (12 Voyager 3.0 LFP units, PCS, BMS, fire protection, 10-yr warranty, spares, remote support) as carried in Rev 3: $1,213,043 actual LNTP payments + $11,778,062 to-go (escalated).
B. Battery installation & integration (owner scope) | 1733346.4632 | 3.028% | 2921177.4072 | 5.103% | 24814849.4434 | Owner-scope work that exists only because of the batteries: 5,557 mh installation labor, 12 foundation pads, fire suppression, GSU-to-BESS conduit and 600 V cable.
C. Battery balance-of-plant (GSUs, EMS/comms, aux power) | 1932801.5973 | 3.376% | 3257315.5329 | 5.69% | 28072164.9763 | Four 3 MVA 13.8 kV/480 V generator step-up transformers, site EMS/communications, AC/DC auxiliary power panels. Vendors often bundle these in a 'turnkey' quote; here they are owner-furnished.
D. Station 360 13.8 kV switching & interconnection facilities | 3846444.3221 | 6.719% | 6482342.9651 | 11.32% | 34554507.9414 | The new 13.8 kV switching station (Sta 360): four Siemens SDV7 1200 A breaker skids with relays/PTs/DC, disconnects, metering transclosures, station service transformer, riser poles, 15 kV cable, duct bank to feeder manholes, ground grid, lighting, control cable.
E. Site development & civil (former landfill site) | 2690784.1287 | 4.7% | 4534729.7677 | 7.921% | 39089237.7091 | Developing a 200 ft x 200 ft yard on a closed construction-debris landfill: clear and grub, 760 ft access road, 24+12 soil borings, 2,520 CY cut, imported fill, trap rock, 14 ft retaining wall, fence, mob/demob.
F. Station 496 feeder protection upgrades (interconnection) | 7253161.7453 | 12.67% | 7253161.7453 | 12.67% | 46342399.4544 | Station 496 protection upgrades required to accept the BESS on four feeders: 20 SEL relays, transfer trip over dark fiber, RTU/SCADA points, removals. Carried at its full approval level incl. its own indirects/AFUDC/contingency.
G. Testing & commissioning | 1262913.6075 | 2.206% | 2128365.434 | 3.718% | 48470764.8884 | Lead commissioning engineer, field test engineers, field SCADA and telecom commissioning.
H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | 4420366.4791 | 7.721% | 7449563.5838 | 13.01% | 55920328.4721 | Engineering (internal and Leidos/VHB), Article 80 siting and legal, environmental permits (DEP post-closure use, SWPPP, Tier II), community outreach, project management, construction reps, land.
I. Taxes, CWIP, builders-risk insurance | 787533.2123 | 1.376% | 1327215.4621 | 2.318% | 57247543.9342 | Property tax, CWIP, sales and use tax on external material, builders all-risk insurance.
J. Risk register | 5300000 | 9.258% | 0 | 0% | 57247543.9342 | Twelve enumerated risk items on Sta 360 (see BOE).
K. Contingency | 2283517 | 3.989% | 0 | 0% | 57247543.9342 | General contingency on Sta 360.
L. Indirects / overheads | 8064672.3584 | 14.09% | 0 | 0% | 57247543.9342 | Corporate indirects: E&S station overhead, general services, non-productive time, payroll benefits, AS&E, MDEC, vehicles, lobby stock.
M. AFUDC | 4680899.1944 | 8.177% | 0 | 0% | 57247543.9342 | Allowance for funds used during construction, Sta 360.
Total - Project 21334 approval level | 57247543.9342 | 100% | 57247543.9342 | 100%
Station 360 direct layers A-E, G-I (sum) | 29665293.6361
Load factor = (Sta 360 directs + J+K+L+M) / Sta 360 directs | 1.6853
Check: loaded total less direct total (should be 0) | 0
Memo: D-Line interconnection, project 24211 (SSF Feb 2024 conceptual, not re-estimated) | 4793000
Memo: Nomad contract fixed price (Exhibit C, cover agreement dated 3/10/2026) | 12106850
Memo: escalation carried on the fixed-price battery line (Rev 3 line 432 less contract balance) | 1130254.65
Note on B24: Solution Selection Form, approved SDC 2/15/2024: 'Conceptual (-25%/+50%) Distribution Scope Cost Estimate: $4.793 million'. Partial funding of $2,085K approved MPAC 8/5/2024. Scope: 5,465 ft circuit extension, 3 manholes, 1,270 ft 6-5in duct bank, 16,395 ft 3-700 cable.
Note on B26: Rev 3 note on seq 432: 'cover agreement dated 12/6/25 = $11,860,850 minus actual cost and downpayment $1,213,042.82, total = $10,647,808'. Line carries $11,778,062, i.e. 10.6% escalation on a price that Exhibit C fixes until Final Acceptance. The $246,000 labor portion of the SOV is not visible on a separate line.

## Unit Costs
Unit costs at each cost boundary (10 MW / 20 MWh, 2-hour)
Nameplate MW | 10
Nameplate MWh | 20
Boundary | Total ($) | $/kW | $/kWh | Multiple of vendor contract | Definition
1. Vendor contract as quoted (Nomad fixed price) | 12106850 | 1210.685 | 605.3425 | 1 | What the vendor calls 'the project cost': containers, batteries, PCS, BMS, fire protection, spares, 7-yr warranty extension, remote support, shipping, supervision, commissioning, training.
2. Battery supply as carried in Rev 3 (contract + actuals + escalation) - Layer A | 12991103.8259 | 1299.1104 | 649.5552 | 1.073 | Rev 3 line 432 + line 445.
3. Battery system installed (Layers A+B+C, direct) | 16657251.8864 | 1665.7252 | 832.8626 | 1.3759 | Adds owner installation labor, pads, fire suppression, GSUs, EMS/comms, aux power. Closest analogue to a 'turnkey BESS' benchmark before soft costs.
4. Station complete, direct (Layers A-E + G-I, no loaders) | 29665293.6361 | 2966.5294 | 1483.2647 | 2.4503 | Adds the 13.8 kV switching station, landfill site development, testing, owner soft costs and taxes.
5. Station 360 approval level (loaded) | 49994382.189 | 4999.4382 | 2499.7191 | 4.1294 | Adds risk, contingency, indirects and AFUDC. Equals ESF 'Hyde Park BESS - Sta. 360 - Rev 3' $49,994,200.
6. Project 21334 approval level (Sta 360 + Sta 496) | 57247543.9342 | 5724.7544 | 2862.3772 | 4.7285 | Adds the Station 496 feeder protection upgrades. Equals ESF Total Rev 3 $57,247,300.
7. All-in including D-Line interconnection 24211 (memo) | 62040543.9342 | 6204.0544 | 3102.0272 | 5.1244 | Adds the 2024 conceptual distribution circuit extension estimate. Not yet re-estimated; treat as indicative.
Battery supply contract as share of project 21334 approval level | 21.15%
Everything that is not the battery contract ($) | 45140693.9342
Interconnection-driven cost, loaded: Layer D + Layer F ($) | 13735504.7104
Interconnection-driven cost incl. D-Line memo ($) | 18528504.7104

## Timeline
Cost and funding history, 2021 - 2026
Date | Event | Value ($) | Type | Basis / source | $/kWh at 20 MWh
2021-06 | Initial Funding Request (IFR) | 200000 | funding | IFR approved 6/11/2021; 15 MW/20 MWh concept; ISD Q3 2025 | 10
2023-05 | IFR Rev 1 | 500000 | funding | Cumulative initial funding $300K + $200K | 25
2023-07 | Vendor indicative pricing, 5 bidders (Site Two, 10 MW/20 MWh) | 18222342 | vendor | Company 3 turnkey indicative price; range $9.59M-$18.22M across bidders | 911.1171
2023-12 | E-23-373 conceptual estimate | 43926100 | estimate | Conceptual -25/+50%; ISD 4/23/2027; 2023 dollars escalated | 2196.305
2024-02 | SSF preferred alternative (BESS + D-Line) | 49200000 | estimate | $44.379M station + $4.793M distribution; SDC 2/15/2024 | 2460
2024-07 | Partial Funding Rev 1 | 4009000 | funding | EPAC 7/10/2024 | 200.45
2026-02 | Partial Funding Rev 2 | 5767000 | funding | PowerPlan 2/18/2026; FF estimate still $43.926M | 288.35
2026-03 | Nomad cover agreement executed | 12106850 | vendor | Fixed price, 12 Voyager units, 10-yr warranty; SOV dated 12/8/2025 | 605.3425
2026-06 | Partial Funding Rev 3 | 8914000 | funding | EPAC 6/25/2026; FF estimate still $43.926M; ISD 12/28/2028 | 445.7
2026-08 | Sta 360 + 496 estimate Rev 0 | 47201100 | estimate | ESF 8/26/2026; battery line carried at ~$6M | 2360.055
2026-09-01 | Estimate Rev 1 | 51867100 | estimate | Battery material increased per project team | 2593.355
2026-09-10 | Estimate Rev 2 | 63640300 | estimate | Battery line reset to cover agreement ($13.1M escalated) + $1.5M relays | 3182.015
2026-09-24 | Estimate Rev 3 (current) | 57247300 | estimate | Relays removed (-$1.5M), SSVT qty 3->1, engineering re-based to $501K + actuals | 2862.365
In-service date drift
As of | Planned ISD
2021-06 | Q3 2025
2023-12 | Apr 2027
2024-02 | Sep 2027
2026-01 | Aug 2028
2026-06 | Dec 2028

## Sept 2026 Walk
September 2026 estimate revision walk (Project 21334 approval level)
Step | Date | Approval level ($) | Change ($) | Driver (from ESF clarifications and 9/1-9/23/2026 email record)
Rev 0 | 2026-08-26 | 47201100 | 0 | Sta 360 built up from E-23-373 quantities and 7/28/2023 indicative pricing; battery material carried at about $6M (PM: 'change the battery cost (line 71) from 6 to 12.1M').
Rev 1 | 2026-09-01 | 51867100 | 4666000 | Per project team, increase battery material cost.
Rev 2 | 2026-09-10 | 63640300 | 11773200 | Battery line reset to Nomad cover agreement and escalated to $13,119,867; $1,545,014 'Relays, P&C systems for batteries' carried from 2023 Company 1 pricing; 3 SSVTs; engineering hours from E-23-373; $609K LNTP actuals shown separately.
Rev 3 | 2026-09-24 | 57247300 | -6393000 | Relays deleted (-$1.5M, duplicated in $300K/breaker Siemens price per P&C Engineering 9/22); SSVT quantity 3 to 1; engineering re-based to $501K to-go plus actuals (9/18); actuals updated to 9/23 ($5.52M); battery line = contract less $1,213,043 paid, escalated.
Reference: full-funding placeholder carried in PF Rev 2 and Rev 3 PAFs |  | 43926100
Rev 3 vs. full-funding placeholder |  | 13321200 | 30.33%

## 2023 Indicative
July 28, 2023 indicative pricing - Site Two (Hyde Park, 10 MW / 20 MWh), five bidders
Bidder | Total indicative price ($) | $/kWh | Notes on scope / exclusions
Company 1 | 11551925 | 577.5963 | 8 Hithium containers, 4 SMA 3950 PCS skids, switchgear $707K; excludes sound mitigation; prevailing wage and IRA compliance; 5-yr warranty; interconnection by Eversource.
Company 2 (Opt 1) | 10532000 | 526.6 | Assumes connection to substation bus (no switchgear); augmentation required year 7; no LTSA/extended warranty; 'Eversource would be responsible for interconnection cost'.
Company 2 (Opt 2) | 9586600 | 479.33 | As Option 1 with lower-cost enclosure option.
Company 3 | 18222342 | 911.1171 | Basis of the E-23-373 estimate. Battery enclosure $10.58M, PCS $0.83M, step-up transformers $0.63M, sound mitigation $0.47M, turnkey civil/installation $4.56M, spares/transport $0.59M.
Company 4 | 11470000 | 573.5 | 'Complete scope' line items; no step-up transformer; no builders risk; local permits only; no below-grade risk; non-union labor.
Company 5 | 13915000 | 695.75 | Highest engineering/PM line ($3.15M) and installation $2.05M.
Low | 9586600
High | 18222342
Median | 11510962.5
Every bidder listed interconnection, permitting beyond local, below-grade risk, sound walls, spares or long-term service as excluded or 'Eversource responsibility'. Source: BESS_Indicative_Pricing.xlsx (attachment to 9/9/2026 email).

## Benchmarks
Published industry benchmarks (filled from research log; see whitepaper references)
Source | Year | Metric | Value | Units | Duration | Dollar year | What is included | Confidence | URL
BloombergNEF battery pack price survey | 2025 | Pack price, stationary storage segment | 70 | $/kWh | n/a | 2025 real | Cells and pack hardware only, ex-works. No PCS, enclosure, BOS, installation or interconnection. | Medium | https://about.bnef.com/insights/clean-transport/lithium-ion-battery-pack-prices-fall-to-108-per-kilowatt-hour-despite-rising-metal-prices-bloombergnef/
BloombergNEF battery pack price survey | 2025 | Pack price, all-segment volume-weighted average | 108 | $/kWh | n/a | 2025 real | Cells and pack hardware only. | Medium | https://about.bnef.com/insights/clean-transport/lithium-ion-battery-pack-prices-fall-to-108-per-kilowatt-hour-despite-rising-metal-prices-bloombergnef/
Anza Renewables pricing insights | 2026 | Distribution-scale AC system price, delivered incl. tariffs, Q1 2026 | 203 | $/kWh | distribution-scale | 2026 nominal | Equipment delivered (DC blocks + PCS). No EPC, civil, station or interconnection. | Medium | https://www.anzarenewables.com/energy-storage-pricing-insights/
BloombergNEF Energy Storage System Cost Survey | 2025 | Turnkey system price, United States | 219 | $/kWh | 4-h reference | 2025 | Racks/DC blocks, PCS, BOS, EMS, integration, installation and commissioning. Excludes grid connection, land, development and owner's costs (scope wording from prior-year summaries; verify in 2025 methodology). | Medium | https://www.bnef.com/insights/38229
BloombergNEF Energy Storage System Cost Survey | 2024 | Turnkey system price, United States | 236 | $/kWh | 4-h reference | 2024 | As above. | Medium | https://www.bnef.com/insights/35543
BloombergNEF Energy Storage System Cost Survey | 2023 | Turnkey system price, global average (range $135-580) | 263 | $/kWh | 4-h reference | 2023 | As above. | Medium | https://www.bnef.com/insights/33081
NREL, Cole et al., Cost Projections for Utility-Scale Battery Storage: 2025 Update (NREL/TP-6A40-93281) | 2025 | Total installed cost, base year 2024, bottom-up model | 334 | $/kWh | 4-h, 60 MW | 2024 (verify) | Pack, PCS, structural and electrical BOS, installation labor, EPC overhead, developer overhead, sales tax, permitting and an interconnection allowance, contingency, profit. Developer perspective; no utility indirects or AFUDC. | High | https://docs.nrel.gov/docs/fy25osti/93281.pdf
EIA / Sargent & Lundy, Capital Cost and Performance Characteristics (AEO2025) | 2024 | Overnight capital cost, 150 MW / 600 MWh | 436 | $/kWh | 4-h, 150 MW | 2023 | EPC plus owner's costs (development, land, permitting, owner's engineering, spares, contingency). Overnight: excludes AFUDC. Interconnection limited to a tie to an assumed nearby substation. $1,744/kW. | High | https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2025.pdf
LBNL, Utility-Scale Solar 2025 edition | 2025 | Empirical all-in battery capex, hybrid PV+storage plants installed 2024 | 458 | $/kWh | avg 3.3-h | 2024 | EIA-860 reported capitalized cost, battery share of hybrid plants. | High | https://emp.lbl.gov/sites/default/files/2025-10/Utility%20Scale%20Solar%202025%20Edition%20Slides.pdf
EIA Form 860, construction cost of generators installed in 2023 | 2023 | Capacity-weighted average construction cost, battery storage (6,841 MW, $9.3B) | 1361 | $/kW | mixed (not stated) | 2023 nominal | Respondent-reported total capitalized construction cost. | High | https://www.eia.gov/electricity/generatorcosts
Wood Mackenzie / ACP, US Energy Storage Monitor | 2026 | Utility-scale system price, Q2 2026 | 916 | $/kW | 4-h implied | 2026 | Turnkey system incl. EPC; interconnection excluded (verify). | Medium | https://cleanpower.org/resources/u-s-energy-storage-monitor/
LBNL, Interconnection cost analysis in ISO-NE (Kemp et al.) | 2023 | Average interconnection cost, storage requests 2018-21 | 230 | $/kW | n/a | nominal | Point of interconnection plus network upgrades from ISO studies. Equals $115/kWh for a 10 MW / 20 MWh system. | High | https://eta-publications.lbl.gov/sites/default/files/iso-ne_interconnection_costs_vfinal.pdf
NV Energy, Reid Gardner BESS (Energy Vault EPC) | 2023 | Utility-owned 220 MW / 440 MWh, 2-h, at former coal site with existing switchyard, $257M | 584 | $/kWh | 2-h, 220 MW | 2022-23 | EPC construction cost using existing interconnection. | Medium | https://en.wikipedia.org/wiki/Reid_Gardner_Battery_Energy_Storage_System
Southern California Edison / Ameresco (CPUC approval Dec 2021) | 2021 | Utility-owned 537.5 MW / 2,150 MWh at three existing substations, $1.226B | 570 | $/kWh | 4-h | 2021 | EPC plus maintenance term; sited at existing substations; emergency-procurement timelines. | High | https://www.cpuc.ca.gov/news-and-updates/all-news/cpuc-approves-energy-storage-contract-for-sce
Hawaiian Electric, Waena BESS, Maui (PUC approval Dec 2023) | 2023 | Utility-owned 40 MW / 160 MWh Tesla Megapack, $82.1M approved (increase pending for tariffs) | 513 | $/kWh | 4-h, 40 MW | 2023 | Purchase and installation at utility-owned site. | High | https://www.energy-storage.news/hawaiian-electric-requests-funds-with-tariffs-expected-to-drive-up-cost-of-tesla-bess/
National Grid Massachusetts, 2018 rate case proposal | 2018 | Proposed utility-owned 14 MW / 56 MWh, $50M | 893 | $/kWh | 4-h, 14 MW | 2018 estimate | Utility capital estimate; build status not confirmed. | Medium | https://www.sec.gov/Archives/edgar/data/0001004315/000100431518000103/a6kannouncments16nov10de.htm
Eversource Martha's Vineyard Phase 1 (D.P.U. 18-155, cancelled 2021) | 2019 | Utility estimate, 4.9 MW / 20 MWh, $15M | 750 | $/kWh | 4-h, 4.9 MW | 2018-19 estimate | Utility capital estimate, indoor building at service center. | Medium | https://www.mass.gov/info-details/utility-owned-large-scale-battery-energy-storage
Eversource Outer Cape BESS, Provincetown (D.P.U. 17-05) | 2022 | Final cost $49M, 24.9 MW / 38 MWh, in service 2022 | 1289 | $/kWh | 1.5-h, 24.9 MW | 2019-22 nominal | Full utility capital: batteries, PCS, site civil, microgrid islanding controls, interconnection, overheads. $1,968/kW. | High | https://www.utilitydive.com/news/eversource-advances-cape-cod-battery-project-defers-13-mile-distribution-l/552171/
Hyde Park boundaries for comparison ($/kWh, from Unit Costs tab)
Nomad equipment only (12 units, PCS, BMS, fire) |  |  | 531.9 | $/kWh
Vendor contract |  |  | 605.3425 | $/kWh
Battery installed (A+B+C) |  |  | 832.8626 | $/kWh
Station complete, direct |  |  | 1483.2647 | $/kWh
Station 360 approval level |  |  | 2499.7191 | $/kWh
Project 21334 approval level |  |  | 2862.3772 | $/kWh
All-in incl. D-Line memo |  |  | 3102.0272 | $/kWh
Retrieved 29 Sep 2026 from search-index excerpts of the cited pages; direct PDF access was blocked in the research environment. Figures tagged High appear in the primary source text; Medium are reported by a reputable secondary source quoting the primary. Verify against the PDFs before external use.
ISO interconnection cost references (LBNL series; ISO-NE Transitional Cluster Study interim, Jun 2026)
LBNL ISO-NE interconnection brief | 2023 | Storage median, studies 2018-21 | 148 | $/kW | n/a | real (2022$ likely) | POI + network upgrades from ISO studies; all-status storage mean ~ $230/kW | High | https://emp.lbl.gov/publications/interconnection-cost-analysis-iso-new
ISO-NE Transitional Cluster Study interim | 2026 | Average interconnection cost, 23 transmission-connected projects (~$3.2B / 4.8 GW) | 664 | $/kW | n/a | 2026 nominal | System network upgrades ~ $2.5B; WCMA > $1,000/kW, SEMA ~ $177/kW; 21 of 26 requests are BESS | High (totals) / Medium (zonal) | https://www.mass.gov/doc/letter-to-iso-ne-on-transitional-cluster-study-interim-results-june-25-2026/download
LBNL NYISO interconnection brief | 2023 | Storage, 1-50 MW requests (vs $32/kW above 250 MW) | 76 | $/kW | n/a | real | Only ISO-level storage cost by size | High | https://emp.lbl.gov/publications/interconnection-cost-analysis-nyiso
LBNL PJM interconnection brief | 2023 | Storage mean, all statuses | 335 | $/kW | n/a | real | Median $63/kW; complete storage ~ $4/kW | High | https://emp.lbl.gov/publications/interconnection-cost-analysis-pjm
LBNL MISO interconnection brief | 2022 | Storage potential cost, 2018-21 | 248 | $/kW | n/a | real |  | High | https://emp.lbl.gov/publications/generator-interconnection-cost
NYSERDA State of Storage | 2025 | Bulk (>5 MW) average installed cost | 524 | $/kWh | n/a | 2025 nominal | Retail front-of-meter standalone $666/kWh | High | https://www.nyserda.ny.gov/
Modo Energy global capex survey | 2026 | Median 2-h system capex (4-h: $201/kWh) | 325 | $/kWh | 2-h | 2026 nominal | Doubling duration cuts ~38%/MWh | Medium | https://modoenergy.com/research/en/global-battery-capex-september-2026-research

## Cost Curve
Battery installed-cost curve and escalation basis (deck slides 10-11)
Series plotted as published. Direct access to eia.gov, bnef.com and energy-storage.news was blocked by the research proxy; values come from search-index excerpts of those pages and carry the confidence tag of the excerpt. Verify against the primary pages before external use.
A. Industry series as published ($/kWh)
Year | Series | $/kWh | Dollar basis | Scope | Confidence | Source
2015 | EIA reported all-in, utility-scale (EIA-860, nominal $/kWh) | 2152 | Nominal, capacity-weighted average energy-capacity cost of batteries installed in the year | Respondent-reported total capitalized construction cost | High | https://www.eia.gov/todayinenergy/detail.php?id=45596
2017 | EIA reported all-in, utility-scale (EIA-860, nominal $/kWh) | 834 | Nominal, capacity-weighted average energy-capacity cost of batteries installed in the year | Respondent-reported total capitalized construction cost | High | https://www.eia.gov/todayinenergy/detail.php?id=45596
2018 | EIA reported all-in, utility-scale (EIA-860, nominal $/kWh) | 625 | Nominal, capacity-weighted average energy-capacity cost of batteries installed in the year | Respondent-reported total capitalized construction cost | High | https://www.eia.gov/todayinenergy/detail.php?id=45596
2022 | BNEF turnkey system, global avg, 4-h ($/kWh, real survey-year) | 324 | Real USD of the survey year | Racks, PCS, BOS, EMS, integration, installation, commissioning; excludes grid connection, land, development, owner's costs | Medium | https://www.bnef.com/insights/30443 ; https://www.bnef.com/insights/33081 ; https://www.bnef.com/insights/35543 ; https://www.bnef.com/insights/38229
2023 | BNEF turnkey system, global avg, 4-h ($/kWh, real survey-year) | 263 | Real USD of the survey year | Racks, PCS, BOS, EMS, integration, installation, commissioning; excludes grid connection, land, development, owner's costs | Medium | https://www.bnef.com/insights/30443 ; https://www.bnef.com/insights/33081 ; https://www.bnef.com/insights/35543 ; https://www.bnef.com/insights/38229
2024 | BNEF turnkey system, global avg, 4-h ($/kWh, real survey-year) | 165 | Real USD of the survey year | Racks, PCS, BOS, EMS, integration, installation, commissioning; excludes grid connection, land, development, owner's costs | Medium | https://www.bnef.com/insights/30443 ; https://www.bnef.com/insights/33081 ; https://www.bnef.com/insights/35543 ; https://www.bnef.com/insights/38229
2025 | BNEF turnkey system, global avg, 4-h ($/kWh, real survey-year) | 117 | Real USD of the survey year | Racks, PCS, BOS, EMS, integration, installation, commissioning; excludes grid connection, land, development, owner's costs | Medium | https://www.bnef.com/insights/30443 ; https://www.bnef.com/insights/33081 ; https://www.bnef.com/insights/35543 ; https://www.bnef.com/insights/38229
2024 | BNEF turnkey system, United States, 4-h | 236 | Real USD of the survey year | As above | Medium | https://www.bnef.com/insights/38229
2025 | BNEF turnkey system, United States, 4-h | 219 | Real USD of the survey year | As above | Medium | https://www.bnef.com/insights/38229
2024 | NREL bottom-up all-in, 4-h 60 MW (2024$), mid-case projection | 334 | 2024 dollars; 2028 point is a linear interpolation between the 2024 base and the 2035 mid case | Pack, PCS, BOS, installation, EPC and developer overhead, sales tax, permitting and interconnection allowance, contingency, profit | High (2024 and 2035 points); derived (2028) | https://docs.nrel.gov/docs/fy25osti/93281.pdf
2028 | NREL bottom-up all-in, 4-h 60 MW (2024$), mid-case projection | 302 | 2024 dollars; 2028 point is a linear interpolation between the 2024 base and the 2035 mid case | Pack, PCS, BOS, installation, EPC and developer overhead, sales tax, permitting and interconnection allowance, contingency, profit | High (2024 and 2035 points); derived (2028) | https://docs.nrel.gov/docs/fy25osti/93281.pdf
2035 | NREL bottom-up all-in, 4-h 60 MW (2024$), mid-case projection | 247 | 2024 dollars; 2028 point is a linear interpolation between the 2024 base and the 2035 mid case | Pack, PCS, BOS, installation, EPC and developer overhead, sales tax, permitting and interconnection allowance, contingency, profit | High (2024 and 2035 points); derived (2028) | https://docs.nrel.gov/docs/fy25osti/93281.pdf
B. Hyde Park points ($/kWh at 20,000 kWh)
Year (decimal) | Point | $/kWh | Basis
2023.5 | 2023 indicative bids, low (Company 2 Opt 2 $9,586,600) | 479 | July 2023 indicative sheet
2023.5 | 2023 indicative bids, high (Company 3 $18,222,342) | 911 | July 2023 indicative sheet
2026.2 | Nomad equipment only ($10,638,000) | 531.9 | Cover agreement SOV
2026.2 | Nomad contract ($12,106,850) | 605.3425 | Cover agreement Exhibit C
2026.75 | Battery as carried in Rev 3, layer A (contract balance escalated + actuals) | 649.5552 | Rev 3 lines 432 + 445
2026.75 | Battery installed, layers A+B+C | 832.8626 | Rev 3 layers A, B, C
C. Adjusting a 4-h, 60-240 MWh index to 2-h, 20 MWh
Input | Value | Note
Duration factor, low | 1.3 | NREL cost structure: pack $/kWh x hours + BOS $/kW; 2-h vs 4-h
Duration factor, high | 1.5 | as above
Size elasticity | -0.173 | Appendix B regression, ln(MWh) coefficient
Reference MWh | 240 | NREL 60 MW x 4 h
Hyde Park MWh | 20
Size factor | 1.5371 | (20/240)^-0.173
Combined factor, low | 1.9982
Combined factor, high | 2.3056
BNEF US turnkey 2025, adjusted low | 437.6086 | vs Nomad equipment $532
BNEF US turnkey 2025, adjusted high | 504.933
NREL 2024 base $334 to 2028 at 3%/yr | 375.9199
NREL 2028, adjusted low | 751.168 | vs Hyde Park installed $833
NREL 2028, adjusted high | 866.7323
Escalation rate | 0.03 | ESF template, approx.
D. Escalation in Rev 3 (ESF Overview row 34, included in directs)
Item | $ | $/kWh | Note
Escalation, Station 360 | 2622100 | 131.105 | ESF Sta 360 Rev 3 Overview
Escalation, Station 496 | 326100 | 16.305 | ESF Total Rev 3 Overview
Escalation, project 21334 | 2948200 | 147.41 | ESF Overview shows $2,948,100 after rounding
of which on the Nomad balance (fixed price) | 1130254.65 | 56.5127 | Rev 3 line 432 less contract balance
of which on other scope | 1817945.35 | 90.8973
Share of approval level | 5.15%
Spend 2027-2028 (Schedule tab) | 38563658 | 1928.1829 | ESF Schedule tab, 2027 + 2028 columns
Escalation from a 12-month slip at the template rate | 1156909.74 | 57.8455 | before AFUDC, PM, indirects
Non-battery material (Materials category less layer A) | 3686996.1741 | 184.3498 | exposure to tariff / commodity moves above 3%
E. Same comparison, same dollars ($/kWh)
Boundary | Nominal as carried | Ex-escalation (2026$) | Benchmark brought to 2028 at the template rate | Note
Vendor contract | 605.3425 | 605.3425 | 239.3072 | BNEF US turnkey 2025 -> 2028
Battery as carried (A) | 649.5552 | 593.0425 | 375.9199 | NREL 4-h 2024$ -> 2028
Battery installed (A+B+C) | 832.8626 | 756.3643 | 751.168 | NREL 2028 adjusted to 2-h, 10 MW (low); high = adjusted high
Station complete, direct | 1483.2647 | 1352.1597 | 505.4435 | EIA/S&L 2023$ -> 2028
Ex-escalation removes the Station 360 escalation from the direct boundaries; the B+C share is allocated pro rata to direct cost across Station 360 layers B to I and is approximate.

## Public Projects
Public project-level BESS costs (44 compiled; 26 used in the regression). Blue = keyed from source; $/kWh, $/kW and duration are formulas.
Project | Owner | Owner type | State | ISO | MW | MWh | COD year | Cost ($) | Cost basis | Scope | Site type | Confidence | Excluded (reason) | Duration (h) | $/kWh | $/kW | Source URL | Notes | In reference class? ($/kWh if yes)
Outer Cape (Provincetown) BESS | Eversource (NSTAR Electric) | IOU | MA | ISO-NE | 25 | 38 | 2022 | 49000000 | final/actual (as reported) | all-in incl. 8,000 sf building, fiber-optic control network and Provincetown loop circuitry (microgrid) | existing municipal site (town transfer station), distribution-connected | Medium |  | 1.52 | 1289.4737 | 1960 | https://provincetownindependent.org/featured/2026/05/13/eversource-will-upgrade-exposed-poles-on-shore-road/ | DPU 17-05 (2017) approved budget range $35-45M; $49M final per Provincetown Independent and capecod.com reporting; cost includes non-battery microgrid/fiber scope | 1289.4737
Nantucket BESS | National Grid (Massachusetts Electric) | IOU | MA | ISO-NE | 6 | 48 | 2019 | 81000000 | final/actual (as reported) | all-in incl. new 15 MW diesel generator and power control house | existing utility site (Bunker Rd), distribution/island | Medium | cost bundles 15 MW diesel generator and control house | 8 | 1687.5 | 13500 | https://www.renewableenergyworld.com/energy-storage/battery/6-mw-48-mwh-battery-storage-system-unveiled-on-nantucket-island-in-massachusetts/ | Tesla Powerpack 8-hour; $81M includes generator - battery-only cost not disclosed; alternative was ~$200M third submarine cable
Martha's Vineyard BESS Phase 1 (cancelled) | Eversource (NSTAR Electric) | IOU | MA | ISO-NE | 4.9 | 20 | 2019 | 15000000 | estimate (DPU 18-155 filing) | all-in utility capital estimate | greenfield adjacent to Oak Bluffs substation | Medium |  | 4.0816 | 750 | 3061.2245 | https://www.microgridknowledge.com/distributed-energy/article/11429907/eversource-pushes-ahead-with-147-mw-battery-project-on-marthas-vineyard | cod_year = DPU approval year (2019); Eversource cancelled project May 2021; never built | 750
Martha's Vineyard BESS Phase 2 (cancelled) | Eversource (NSTAR Electric) | IOU | MA | ISO-NE | 9.8 | 64 | 2019 | 28000000 | estimate (DPU 18-155 filing) | all-in utility capital estimate | greenfield adjacent to Oak Bluffs substation | Medium |  | 6.5306 | 437.5 | 2857.1429 | https://www.microgridknowledge.com/distributed-energy/article/11429907/eversource-pushes-ahead-with-147-mw-battery-project-on-marthas-vineyard | cod_year = DPU approval year (2019); planned COD 2023; cancelled May 2021 | 437.5
Sterling MLD Chocksett Road BESS | Sterling Municipal Light Department | muni/coop | MA | ISO-NE | 2 | 3.9 | 2016 | 2700000 | final/actual (as reported) | turnkey battery + installation (NEC Energy Solutions) | existing substation | Medium |  | 1.95 | 692.3077 | 1350 | https://www.cesa.org/resource-library/resource/project-overview-sterling-municipal-energy-storage-project/ | $1.4M MA DOER resiliency grant + $250k DOE grant; commissioned Dec 2016 | 692.3077
Pomona (Ladentown) BESS | Orange & Rockland Utilities (Con Edison) | IOU | NY | NYISO | 3 | 12 | 2021 | 7400000 | final/actual (utility press release) | all-in utility-owned (developed/built by Key Capture Energy) | existing substation (adjacent Ladentown substation, O&R property) | High |  | 4 | 616.6667 | 2466.6667 | https://www.oru.com/en/about-us/media-center/news/2021/04-20/oru-key-capture-energy-begins-operations-at-orus-first-energy-storage-facility | 4-hour; first O&R storage facility | 616.6667
Salem Smart Power Center | Portland General Electric | IOU | OR | non-ISO (WECC NW) | 5 | 1.25 | 2013 | 23000000 | final/actual (demonstration total) | all-in demonstration incl. building, microgrid, smart-grid controls; DOE cost-share (PNW Smart Grid Demo) | greenfield industrial site (SE Salem) | High | 2013 demonstration incl. building and smart-grid controls | 0.25 | 18400 | 4600 | https://investors.portlandgeneral.com/news-releases/news-release-details/portland-general-electric-opens-salem-smart-power-center-along | EnerDel Li-ion 5 MW/1.25 MWh; R&D demo - not representative of commercial cost
Waena BESS (Maui) | Hawaiian Electric (Maui Electric) | IOU | HI | non-ISO (island) | 40 | 160 | 2027 | 82100000 | approved budget/estimate (HPUC Dec 2023) | all-in purchase and installation; EPRM cost recovery | greenfield on utility land adjacent Waena switchyard | High |  | 4 | 513.125 | 2052.5 | https://www.sec.gov/Archives/edgar/data/0000354707/000035470726000054/he-20260630.htm | Original 2020 estimate $60M; July 2025 PUC allowed recovery up to +20% over estimate for tariff-driven cost changes; $27.2M incurred as of 6/30/2026; Tesla Megapack
Arlington Microgrid | Snohomish County PUD | muni/coop | WA | non-ISO (WECC NW) | 1 | 1.4 | 2020 | 12000000 | final/actual (as reported) | all-in microgrid incl. 500 kW solar, Clean Energy Center building, V2G, controls | greenfield at PUD Arlington office site | Medium | microgrid incl. solar, building, V2G | 1.4 | 8571.4286 | 12000 | https://www.snopud.com/community-environment/our-energy-future/projects/arlington-microgrid-project/ | $3.5M WA Clean Energy Fund grant; battery-only cost not separated
Reid Gardner BESS | NV Energy (Berkshire Hathaway Energy) | IOU | NV | non-ISO (WECC; EIM) | 220 | 440 | 2023 | 257000000 | final/actual (as reported) | all-in | coal-site (retired Reid Gardner Generating Station) | Medium |  | 2 | 584.0909 | 1168.1818 | https://reviewjournal.com/business/energy/nv-energy-cuts-ribbon-on-257m-facility-meant-to-boost-solar-energy-3040299 | Energy Vault EPC; ~40% (~$100M) of cost offset by IRA tax credits; PUCN approved 2022
Constable (Evergreen) BESS | Portland General Electric | IOU | OR | non-ISO (WECC NW) | 75 | 300 | 2024 | 156000000 | final/actual (Electric Utility Plant recorded incl. AFUDC, 10-K) | rate-base capital incl. AFUDC (EPC by Mortenson) | greenfield (Hillsboro) | High |  | 4 | 520 | 2080 | https://www.sec.gov/Archives/edgar/data/784977/000078497725000012/por-20241231.htm | 4-hour; COD Dec 2024
Seaside BESS | Portland General Electric | IOU | OR | non-ISO (WECC NW) | 200 | 800 | 2025 | 360000000 | contract price (fixed-cost build-transfer agreement, excl. AFUDC) | EPC/BTA turnkey excl. AFUDC | greenfield (North Portland) | High |  | 4 | 450 | 1800 | https://www.sec.gov/Archives/edgar/data/784977/000078497725000012/por-20241231.htm | Eolian BTA; OPUC Order 25-417 rate base $220M net of $125M ITC; COD July 2025
Essex Solar + Storage | Green Mountain Power | IOU | VT | ISO-NE | 2 | 8 | 2022 | 14300000 | estimate (development + interconnection) | all-in incl. 4.9 MW solar (18,326 panels) and interconnection | greenfield | Medium | bundles 4.9 MW solar | 4 | 1787.5 | 7150 | https://vtdigger.org/2022/09/29/green-mountain-power-expands-battery-storage-to-avoid-buying-energy-from-the-grid/ | Tesla Powerpack 2 MW/4-hour; cost includes solar - not separable
Northern New York (Chateaugay) BESS | New York Power Authority | other (state power authority) | NY | NYISO | 20 | 20 | 2023 | 29800000 | approved budget (NYPA Trustees) | all-in | existing substation (adjacent NYPA Willis substation) | High |  | 1 | 1490 | 1490 | https://nypa.gov/news/press-releases/2023/20230825-utility | 1-hour system; initial $23.8M approval + $6M added | 1490
Ozone Park BESS | Con Edison | IOU | NY | NYISO | 1.5 | 12 | 2019 | 15000000 | estimate (utility spokesman: 'about $15 million') | all-in facility | utility property in Ozone Park, Queens (distribution) | Low |  | 8 | 1250 | 10000 | https://ny1.com/nyc/queens/news/2019/05/10/con-ed-creates-battery-farm-to-address-summer-strain-on-power-grid | 8-hour; some sources cite 2 MW; cost figure is an informal spokesman statement | 1250
Hot Springs Microgrid | Duke Energy Progress | IOU | NC | non-ISO (SERC) | 4.4 |  | 2023 | 14500000 | final/actual (as reported) | all-in microgrid incl. 2 MW(AC) solar and controls | greenfield (town of Hot Springs) | Medium | bundles 2 MW solar; MWh not confirmed |  |  | 3295.4545 | https://www.theassemblync.com/business/hot-springs-microgrid-duke-energy/ | Battery cited as 4 MW/16 MWh in NCUC filings and 4.4 MW in Duke releases; MWh left blank (not confirmed in retrieved excerpts); 2017 announcement put Hot Springs + Asheville combined at ~$30M
Virginia battery pilot portfolio (Scott Solar 10+2 MW, New Kent 2 MW, Hanover/Ashland 2 MW) | Dominion Energy Virginia | IOU | VA | PJM | 16 |  | 2022 | 33000000 | estimate (SCC filing, 2019) | all-in construction | mixed: solar co-located (Scott Solar) and substation sites | Medium |  |  |  | 2062.5 | https://www.tdworld.com/distributed-energy-resources/energy-storage/article/20972946/dominion-energy-announces-battery-storage-pilot-projects | Scott Solar units are 4-hour (48 MWh); MWh for 2 MW units not confirmed so total left blank; SCC approved Feb 2020; Scott Solar operational 2022
Glacier BESS | Puget Sound Energy | IOU | WA | non-ISO (WECC NW) | 2 | 4.4 | 2016 | 11200000 | final/actual (PSE $7.4M + $3.8M state grant) | all-in demonstration | existing substation (adjacent Glacier substation) | High |  | 2.2 | 2545.4545 | 5600 | https://www.pse.com/en/pages/grid-modernization/glacier-demo-project | WA Dept of Commerce $3.8M Smart Grid grant; PNNL performance reports | 2545.4545
Chugach BESS (Southcentral Power Project site) | Chugach Electric Association (75%) / Matanuska Electric Association (25%) | muni/coop | AK | non-ISO (Railbelt) | 40 | 80 | 2024 | 65000000 | final/actual (as reported) | all-in | existing generation site (adjacent SPP plant) | High |  | 2 | 812.5 | 1625 | https://www.chugachelectric.com/your-cooperative/news-community/news-releases/2024/10/7/battery-energy-storage-system-officially-commissioned | 24 Tesla Megapacks; ADN reported $63M in 2023, $65M at 2024 commissioning; may qualify for ITC | 812.5
Trenton Channel Energy Center BESS | DTE Electric | IOU | MI | MISO | 220 | 880 | 2026 | 460000000 | approved estimate (MPSC, 2024) | all-in incl. new substation and transmission tie | coal-site (retired Trenton Channel plant) | Medium |  | 4 | 522.7273 | 2090.9091 | https://www.energy-storage.news/us-utility-dte-starts-220mw-880mwh-bess-project-at-michigan-coal-plant-site/ | Powin LFP; ~$140M IRA tax credits offset; planned COD 2026
Roadrunner Reserve (Phase 1) | Tucson Electric Power | IOU | AZ | non-ISO (WECC SW) | 200 | 800 | 2025 | 294000000 | estimate at announcement (2023) | EPC turnkey (DEPCOM Power) | greenfield (SE Tucson) | Medium |  | 4 | 367.5 | 1470 | https://tucson.com/news/local/business/article_95df9266-623a-11ee-8f58-8bdd862facf6.html | TEP later described the first 200 MW as a '$350 million investment' (tep.com) - unclear whether $350M is updated Phase 1 cost or Phase 2; both reported
Roadrunner Reserve 2 (Phase 2) | Tucson Electric Power | IOU | AZ | non-ISO (WECC SW) | 200 | 800 | 2026 | 350000000 | estimate (utility statement) | all-in | existing site expansion (adjacent Phase 1) | Medium |  | 4 | 437.5 | 1750 | https://www.tep.com/roadrunner/ | Online June 2026 per TEP; combined 400 MW / 1,600 MWh
Minnesota utility-owned distribution battery program (200 MW) | Xcel Energy (Northern States Power-MN) | IOU | MN | MISO | 200 |  | 2026 | 430000000 | approved program budget (MPUC, 2026) | rate-base program capital (multiple distribution sites) | distribution substations (various) | Medium | program budget, MWh not stated |  |  | 2150 | https://www.utilitydive.com/news/minnesota-approves-xcels-controversial-utility-owned-virtual-power-plant/816673/ | Programmatic, not a single project; PUC approved 200 MW with interim assessment at 50 MW; duration not confirmed in retrieved excerpt
Harding Street BESS | Indianapolis Power & Light (AES Indiana) | IOU | IN | MISO | 20 | 20 | 2016 | 25000000 | estimate at announcement (2015) | all-in | existing generation site (Harding Street station) | Medium |  | 1 | 1250 | 1250 | https://www.utilitydive.com/news/indianapolis-power-light-to-invest-25m-in-storage-facility/399502/ | First MISO grid battery; primary frequency response; placed in rate base | 1250
Kingsbery Community Solar + Storage | Austin Energy | muni/coop | TX | ERCOT | 1.5 | 3 | 2016 | 3000000 | final/actual (as reported) | all-in battery incl. install at community solar site | existing substation (Kingsbery) with community solar | Medium |  | 2 | 1000 | 2000 | https://www.statesman.com/story/news/2016/09/04/austin-energy-poised-to-test-its-first-energy-storage-system/9995279007/ | $1M TCEQ grant; Tesla battery (Younicos integrator) | 1000
Nova Scotia BESS portfolio (Bridgewater, Waverley, White Rock; 3 x 50 MW) [CANADA] | Nova Scotia Power (Emera) with Wskijnu'k Mtmo'taqnuow Agency | IOU | NS (Canada) | non-ISO (NS Power) | 150 | 600 | 2026 | 258000000 | approved budget (NSUARB) incl. AFUDC | rate-base capital incl. AFUDC | greenfield (3 sites) | High |  | 4 | 430 | 1720 | https://www.cbc.ca/news/canada/nova-scotia/nsp-battery-storage-system-approved-1.7235197 | Reported C$354M incl AFUDC; converted at ~0.73 USD/CAD (approximate); C$109M NRCan grant + C$138.2M CIB loan; 4-hour
Guam ESS (Agana 24 MW/6 MWh + Talofofo 16 MW/16 MWh) | Guam Power Authority | muni/coop | GU | non-ISO (island) | 40 | 22 |  | 43000000 | contract price (turnkey, 2017) | EPC turnkey (LG CNS) | existing substations | Medium |  | 0.55 | 1954.5455 | 1075 | https://www.utilitydive.com/news/lg-subsidiary-will-install-40-mw-of-batteries-on-guam/444490/ | Two systems under one $43M contract; 12-month delivery from 2017; reported operating by 2021; COD year not confirmed in excerpts | 1954.5455
Fairhaven BESS | Baltimore Gas & Electric (Exelon) | IOU | MD | PJM | 2.5 | 9.74 | 2023 | 16161336 | final/actual (reported to MD PSC) | all-in utility-owned | existing substation (Fairhaven) | High |  | 3.896 | 1659.2747 | 6464.5344 | https://psc.maryland.gov/wp-content/uploads/Energy-Storage-Pilot-Program-Interim-Report.pdf | Initial estimate $9,841,000; actual $16,161,336; MWh cited as 7.1 (proposal) and 9.74 (interim report); PJM frequency regulation + winter peak | 1659.2747
Regina BESS [CANADA] | SaskPower | other (crown utility) | SK (Canada) | non-ISO (SaskPower) | 20 |  | 2024 | 25000000 | final/actual (as reported) | all-in | greenfield (Regina) | High |  |  |  | 1250 | https://www.cbc.ca/news/canada/saskatchewan/saskpower-battery-energy-storage-1.7253756 | Reported C$34M (initial estimate C$26M); converted at ~0.74 USD/CAD; federal contribution C$13.1M; MWh not confirmed in retrieved excerpt
Stafford Hill Solar + Storage (Rutland) | Green Mountain Power | IOU | VT | ISO-NE | 4 | 3.4 | 2015 | 4200000 | final/actual (storage component) | battery + inverters (storage share of $10M project) | greenfield (capped landfill) with 2.5 MW solar | Medium |  | 0.85 | 1235.2941 | 1050 | https://www.cleanegroup.org/initiatives/technical-assistance-fund/featured-installations/stafford-hill/ | Mixed chemistry: 2 MW/1 MWh Li-ion + 2 MW/2.4 MWh advanced lead-acid; solar portion ~$5.77M | 1235.2941
Westside Canal BESS Phase 2a | San Diego Gas & Electric (Sempra) | IOU | CA | CAISO | 119 |  | 2024 | 267900000 | approved estimate (CPUC) | all-in utility-owned | existing site (adjacent Westside Canal Phase 1, Imperial Valley) | High |  |  |  | 2251.2605 | https://www.sempra.com/newsroom/press-releases/sdge-expands-energy-storage-capabilities-enhance-grid-resiliency-and | COD Dec 2024; duration/MWh not confirmed in retrieved excerpt (SDG&E portfolio is predominantly 4-hour)
Westside Canal BESS Phase 2b (expansion) | San Diego Gas & Electric (Sempra) | IOU | CA | CAISO | 100 |  | 2025 | 224500000 | approved estimate (CPUC, Mar 2025) | all-in utility-owned | existing site expansion (Imperial Valley) | High |  |  |  | 2245 | https://www.sempra.com/newsroom/press-releases/sdge-expands-energy-storage-capabilities-enhance-grid-resiliency-and | Adds 100 MW to existing 131 MW facility; projected fully operational June 2025; MWh not confirmed
Smarter Network Storage (Leighton Buzzard) [UK] | UK Power Networks | IOU (regulated DNO) | Bedfordshire (UK) | GB (National Grid ESO) | 6 | 10 | 2014 | 29000000 | final (project budget) | all-in demonstration incl. trials/R&D (Low Carbon Networks Fund) | existing primary substation | High | R&D demonstration incl. trials | 1.6667 | 2900 | 4833.3333 | https://innovation.ukpowernetworks.co.uk/projects/smarter-network-storage-sns | Reported GBP 18.7M; converted at ~1.55 USD/GBP (2014); Samsung SDI/S&C/Younicos
Dalrymple ESCRI BESS [AUSTRALIA] | ElectraNet (transmission network service provider) | IOU (regulated TNSP) | SA (Australia) | NEM | 30 | 8 | 2018 | 22200000 | final/actual (as reported) | all-in | existing substation (Dalrymple) | High |  | 0.26667 | 2775 | 740 | https://arena.gov.au/news/grid-scale-escri-battery-charges-up-in-south-australia/ | Reported A$30M; converted at ~0.74 USD/AUD (2018); A$12M ARENA grant later repaid; operated by AGL under lease | 2775
Oneida Energy Storage [CANADA] | Northland Power / Six Nations of the Grand River / NRStor / Aecon | IPP | ON (Canada) | IESO | 250 | 1000 | 2025 | 511000000 | final/actual (reported ~C$700M vs C$800M budget) | all-in | greenfield (Haldimand County) | High |  | 4 | 511 | 2044 | https://www.northlandpower.com/en/news/press-release/northland-power-announces-commercial-operations-at-oneida-energy-storage-project-canadas-largest-bat.aspx | Converted at ~0.73 USD/CAD; CIB loan; IESO capacity contract; COD May 2025
SwRI Solar + Storage (5 MW PV + 10 MW BESS) | CPS Energy | muni/coop | TX | ERCOT | 10 | 10 | 2019 | 16300000 | approved budget (CPS Board) | all-in incl. 5 MW solar | greenfield (SwRI land, San Antonio) | Medium | bundles 5 MW solar | 1 | 1630 | 1630 | https://www.powermag.com/press-releases/cps-energy-launches-solar-energy-and-battery-storage-project/ | $3M TCEQ NTIG grant; cost includes solar - not separable
SCE substation BESS portfolio (Springvale 225 MW, Hinson 200 MW, Etiwanda 112.5 MW) | Southern California Edison | IOU | CA | CAISO | 537.5 | 2150 | 2022 | 1226000000 | contract price (EPCM contract, CPUC-authorized Dec 2021) | EPC + maintenance (Ameresco EPCM) | existing substations | High |  | 4 | 570.2326 | 2280.9302 | https://www.cpuc.ca.gov/news-and-updates/all-news/cpuc-approves-energy-storage-contract-for-sce | 4-hour; emergency reliability procurement under 2021 Governor's proclamation; aggregate of three sites
Whitehorse Grid-Scale BESS [CANADA] | Yukon Energy | other (crown utility) | YT (Canada) | non-ISO (Yukon isolated grid) | 7 | 40 |  | 23600000 | estimate (2020$, +/-30%, Yukon Utilities Board application) | all-in | greenfield (Whitehorse) | High |  | 5.7143 | 590 | 3371.4286 | https://yukonenergy.ca/energy-in-yukon/projects-facilities/battery-storage | Reported C$31.7M; converted at ~0.745 USD/CAD; C$16.5M federal grant; SunGrid Solutions EPC; COD not confirmed in retrieved excerpts (planned 2023) | 590
Rock Hill (Asheville) substation BESS | Duke Energy Progress | IOU | NC | non-ISO (SERC) | 9 |  | 2020 | 15000000 | estimate (upper bound: 'less than $15 million') | all-in | existing substation (Rock Hill, Sweeten Creek Rd) | Medium |  |  |  | 1666.6667 | https://news.duke-energy.com/releases/north-carolinas-largest-battery-system-now-operating-at-duke-energy-substation | Cost is an upper bound; MWh not confirmed; 2017 announcement: Hot Springs + Asheville ~$30M combined
Morro Bay BESS (proposed, not built) | Vistra | IPP | CA | CAISO | 600 | 2400 |  | 550000000 | estimate ($500-600M, developer statement) | all-in | existing retired gas plant site (Morro Bay) | Low | proposed, no COD, developer statement | 4 | 229.1667 | 916.6667 | https://esterobaynews.com/featured-stories/vistra-proposes-worlds-biggest-battery-storage-facility/ | Midpoint of $500-600M range; local approval not obtained; project status uncertain/reportedly shelved; cod_year blank
Kwinana BESS Stage 1 [AUSTRALIA] | Synergy (WA state-owned utility) | other (state-owned utility) | WA (Australia) | SWIS/WEM | 100 | 200 | 2023 | 103500000 | final (as reported) | all-in | coal-site (decommissioned Kwinana Power Station) | Medium |  | 2 | 517.5 | 1035 | https://www.pv-magazine-australia.com/2023/05/15/wa-plans-bigger-batteries-as-200-kwinana-system-put-to-test/ | Reported A$155M (USD 103.5M as stated by source); state/federal funded
WindCharger [CANADA] | TransAlta Renewables | IPP | AB (Canada) | AESO | 10 | 20 | 2020 | 11000000 | final/actual (total capital cost) | all-in | existing wind farm site (Summerview II) | Medium |  | 2 | 550 | 1100 | https://renewablesnow.com/news/transalta-renewables-10-mw-wind-powered-battery-reaches-cod-in-alberta-717754/ | Reported C$14.5M (USD 11M as stated by source); ~50% ERA grant; Tesla Megapack
Weld Energy Storage (for Platte River Power Authority) | Weld Energy Storage LLC (NextEra Energy Resources) | IPP | CO | non-ISO (WECC) |  | 400 | 2026 | 141000000 | estimate (reported project cost) | all-in | greenfield (Weld County) | Medium |  |  | 352.5 |  | https://coloradobiz.com/platte-river-energy-storage-weld-county-battery-project/ | IPP-owned under long-term storage agreement with Platte River; MW not confirmed in retrieved excerpt; planned COD late 2026
Glenarm BESS (for Pasadena Water & Power) | Glenarm BESS LLC (EPC Energy SPE) | IPP | CA | CAISO | 25 | 100 | 2027 | 55300000 | contract price (15-year services contract value) | contract value - not a construction cost | existing gas plant site (Glenarm Power Plant) | Medium | 15-year contract value, not capex | 4 | 553 | 2212 | https://pasadenanow.com/main/city-committee-unanimously-approves-100-million-long-term-contracts-for-renewable-energy-battery-energy-storage | $9.6M CEC DEBA grant to PWP; 4-hour; planned COD 2027; treat as contract value not capex
Reference class (utility-owned, <=100 MWh, not excluded): median $/kWh | [14 empty] | 1242.6471 | 16
Column T flags the reference class (utility-owned, <= 100 MWh, not excluded); the median and count above are live formulas. The Statistics tab carries the Python run values as of 29 Sep 2026.

## 2026$ Adjustment
Dollar-year adjustment of the public comparables to 2026 (deck slides 12-13)
cost_2026 = cost_nominal x [ s x I(2026)/I(y) + (1 - s) x (1 + g)^(2026 - y) ] s = battery share of the comparable, I = battery index, g = non-battery construction escalation. Blue = inputs.
Battery share s | 0.4
Construction escalation g | 3.5%
Index selector (1 installed, 2 pack, 3 LCOS) | 1
A. Battery indices as published ($/kWh; LCOS $/MWh)
Year | Installed all-in (EIA-860, LBNL) | BNEF pack (real) | Lazard LCOS midpoint | Note
2015 | 2152 | 373 | 245 | published
2016 | 1493 | 288 | 245 | published
2017 | 834 | 214 | 245 | published
2018 | 625 | 176 | 245 | published
2019 | 597 | 156 | 245 | published
2020 | 569 | 137 | 191 | published
2021 | 542 | 132 | 202 | published
2022 | 514 | 151 | 212 | published
2023 | 486 | 139 | 222 | published
2024 | 458 | 115 | 233 | published
2025 | 458 | 108 | 185 | published
2026 | 458 | 108 | 251 | published
Sources: EIA Today in Energy #45596 (2015-18); LBNL Utility-Scale Solar 2025 (2024); BNEF Lithium-Ion Battery Price Survey 2015-2025; Lazard LCOS v5.0, v6.0, LCOE+ 2024-2026 (unsubsidized 100 MW / 4-h range midpoints). Black values are linear interpolations; LCOS and installed held flat outside their published span.
B. Reference class (13 utility-owned comparables, <= 100 MWh)
Project | COD year | Nominal $/kWh | Index at COD | Index 2026 | Factor | 2026$ $/kWh | Naive (whole cost deflated)
Martha's Vineyard BESS Phase 2 (cancelled) | 2019 | 437.5 | 597 | 458 | 1.0702 | 468.2279 | 335.6365
Pomona (Ladentown) BESS | 2021 | 616.7 | 542 | 458 | 1.0506 | 647.9168 | 521.1229
Sterling MLD Chocksett Road BESS | 2016 | 692.3 | 1493 | 458 | 0.96907 | 670.8839 | 212.3733
Martha's Vineyard BESS Phase 1 (cancelled) | 2019 | 750 | 597 | 458 | 1.0702 | 802.6764 | 575.3769
Chugach BESS (Southcentral Power Project site) | 2024 | 812.5 | 458 | 458 | 1.0427 | 847.2222 | 812.5
Kingsbery Community Solar + Storage | 2016 | 1000 | 1493 | 458 | 0.96907 | 969.0652 | 306.7649
Stafford Hill Solar + Storage (Rutland) | 2015 | 1235.3 | 2152 | 458 | 0.96111 | 1187.2616 | 262.9031
Ozone Park BESS | 2019 | 1250 | 597 | 458 | 1.0702 | 1337.794 | 958.9615
Harding Street BESS | 2016 | 1250 | 1493 | 458 | 0.96907 | 1211.3315 | 383.4561
Outer Cape (Provincetown) BESS | 2022 | 1289.5 | 514 | 458 | 1.0449 | 1347.4424 | 1149.0097
Fairhaven BESS | 2023 | 1659.3 | 486 | 458 | 1.0422 | 1729.2983 | 1563.7025
Glacier BESS | 2016 | 2545.5 | 1493 | 458 | 0.96907 | 2466.7555 | 780.8701
Dalrymple ESCRI BESS [AUSTRALIA] | 2018 | 2775 | 625 | 458 | 1.0832 | 3005.895 | 2033.52
Median |  | 1235.3 |  |  |  | 1187.2616 | 575.3769
Hyde Park installed $833, percentile |  | 38.46% |  |  |  | 30.77%
Hyde Park station complete direct $1,483, percentile |  | 76.92% |  |  |  | 76.92%
Hyde Park approval $2,862, percentile |  | 100% |  |  |  | 92.31%
C. New York distribution-scale cohort (not in the regression; nominal dollars of the year shown)
Project | Owner | MW | MWh | COD year | Cost $ | $/kWh | $/kW | Hours | Cost basis | Confidence | Source
NineDot Arthur Kill Road (two 4.9 MW systems) | NineDot Energy | 9.8 | 39.1 | 2025 | 43384000 | 1109.5652 | 4426.9388 | 3.9898 | NYCIDA project budget (inducement resolution, Apr 2024) | High | https://edc.nyc/sites/default/files/2025-03/GB%20Arthur%20Kill%20Storage%20LLC%20-%20Inducement%20and%20Authorizing%20Resolution%20April%202024.pdf
Elevate Renewables, 4401 Victory Blvd, Staten Island | Elevate Renewables (ArcLight) | 15.1 | 60.4 | 2025 | 31650000 | 524.0066 | 2096.0265 | 4 | NYCIDA total project cost (public hearing notice, Apr 2024) | High | https://edc.nyc/sites/default/files/2024-03/IDA-Public-Hearing-Notice-April-18-2024.pdf
Soltage Brigis 1A, Maspeth, Queens | Soltage | 5 | 20 | 2025 | 16104493 | 805.2246 | 3220.8986 | 4 | NYCIDA total project cost (public hearing notice, Mar 2024); 4-h duration assumed (MWh not stated) | Medium (cost High; duration assumed) | https://edc.nyc/sites/default/files/2024-02/IDA-Public-Hearing-Notice-March-7-2024-Public-Hearing.pdf
NineDot 28-project NYC portfolio (financing proxy) | NineDot Energy | 124 | 494 | 2027 | 431000000 | 872.4696 | 3475.8065 | 3.9839 | Natixis construction/term loan + tax-credit bridge + LC facility, Feb 2026; a floor on total cost, not the cost itself | Low-Medium (financing, not capex) | https://www.prnewswire.com/news-releases/natixis-corporate--investment-banking-acts-as-sole-lead-arranger-and-bookrunner-for-ninedot-energy-in-431-million-financing-of-28-battery-energy-storage-systems-portfolio-in-new-york-city-302681842.html
NYSERDA retail (<= 5 MW) average total installed cost, 2022-23 installs | NYSERDA program average |  |  | 2023 |  | 567 |  |  | New York's 6 GW Energy Storage Roadmap, NYSERDA/DPS, Dec 2022 | High | https://www.nyserda.ny.gov/-/media/Project/Nyserda/Files/Programs/Energy-Storage/ny-6-gw-energy-storage-roadmap.pdf
NYSERDA retail (<= 5 MW) average total installed cost, 2020-21 installs | NYSERDA program average |  |  | 2021 |  | 464 |  |  | as above | High | https://www.nyserda.ny.gov/-/media/Project/Nyserda/Files/Programs/Energy-Storage/ny-6-gw-energy-storage-roadmap.pdf
Con Edison two-part test (CESIR), NY-BEST / NYSEIA filing 11 Mar 2026, Case 24-E-0621 |  | 161 |  |  | 21000000 |  |  |  | average interconnection upgrade cost per project across 34 projects after the test; about $4,400/kW | Medium | https://www.utilitydive.com/news/battery-developers-local-officials-ask-new-york-to-roll-back-con-edison-be/815115/
New York distribution-connected cohort assembled after a review comment that many more projects have been built in New York (NineDot Energy and others). Values from search-index excerpts of the cited documents; edc.nyc, nyserda.ny.gov, canarymedia.com and mgrid.org were blocked by the research proxy.

## Statistics
Statistical evaluation results (values from stats_model.py and mc_model.py, 29 Sep 2026)
Reference class: utility-owned, <=100 MWh
n | 13
Median $/kWh | 1235.2941
Q25 $/kWh | 750
Q75 $/kWh | 1289.4737
Min $/kWh | 437.5
Max $/kWh | 2775
Hyde Park percentile in class: Vendor contract $605 | 7.692%
Hyde Park percentile in class: Battery installed $833 | 38.46%
Hyde Park percentile in class: Station complete, direct $1,483 | 76.92%
Hyde Park percentile in class: Approval level $2,862 | 100%
Regression: ln($/kWh) ~ ln(MWh) + ln(duration) + year (OLS, HC1 errors)
n | 26
R-squared | 0.64507
Adjusted R-squared | 0.59667
Residual SD (log) | 0.36101
Intercept: coefficient | 7.6194 | SE 0.252, p = 0.000
Size elasticity (ln MWh): coefficient | -0.17311 | SE 0.069, p = 0.012
Duration elasticity (ln hours): coefficient | -0.29238 | SE 0.122, p = 0.016
Year (per year after 2020): coefficient | 0.014876 | SE 0.036, p = 0.678
Prediction for 20 MWh, 2-h, 2028: P50 $/kWh | 1115.5755
80% prediction interval, low | 611.0938
80% prediction interval, high | 2036.5265
Hyde Park percentile of predictive distribution: Vendor contract | 9.648%
Hyde Park percentile of predictive distribution: Battery installed | 26.69%
Hyde Park percentile of predictive distribution: Station complete, direct | 72.8%
Hyde Park percentile of predictive distribution: Approval level | 97.76%
Monte Carlo on cost layers (20,000 trials; risk register and contingency not added on top)
Base ranges: P10 total ($) | 48910799.6142
Base ranges: P50 total ($) | 51293414.5062
Base ranges: P80 total ($) | 53040842.9069
Base ranges: P90 total ($) | 53991966.9619
Base ranges: reserve to reach P80 above deterministic base ($) | 3376815.9726 | carried risk + contingency = $7,583,517
Base ranges: probability total exceeds $57.2M approval level | 0.31%
Base ranges: battery contract share, P50 | 24.24%
Wide (Class 5-like) ranges: P10 total ($) | 50163521.9744
Wide (Class 5-like) ranges: P50 total ($) | 53420558.0185
Wide (Class 5-like) ranges: P80 total ($) | 55912637.4164
Wide (Class 5-like) ranges: P90 total ($) | 57312478.6438
Wide (Class 5-like) ranges: reserve to reach P80 above deterministic base ($) | 6248610.4821 | carried risk + contingency = $7,583,517
Wide (Class 5-like) ranges: probability total exceeds $57.2M approval level | 10.37%
Wide (Class 5-like) ranges: battery contract share, P50 | 23.4%
Layer standard deviation, $ (base / wide)
Layer A | 173279.1825 | wide: 239,415
Layer B | 326886.1023 | wide: 465,344
Layer C | 176401.1307 | wide: 238,386
Layer D | 456422.8798 | wide: 617,589
Layer E | 934979.6186 | wide: 1,311,665
Layer F | 799004.5538 | wide: 1,076,023
Layer G | 159057.4905 | wide: 217,468
Layer H | 514608.6855 | wide: 742,591
Layer I | 43557.1508 | wide: 58,740

## Line Items
Estimate | CBS1 | CBS4 | Seq | Description | Qty | Unit | Direct Cost ($) | Manhours | Note | Layer | Layer code
Hyde Park BESS - Sta. 496 - Rev 2 | 03 | 03.01.00.00 | 0 | SCS, Internal, Traditional | 1 | ls | 5456.8722 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 03 | 03.02.00.00 | 0 | SCS, External, Traditional | 1 | ls | 8185.3083 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 04 | 04.01.00.00 | 0 | Siting, Internal, Application | 1 | ls | 17393.7802 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 04 | 04.02.00.00 | 0 | Siting, External, Application | 1 | ls | 156544.0222 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 05 | 05.02.01.00 | 238 | Engr. Station - Eversource | 40 | mh | 2719.5623 | 40 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 05 | 05.02.02.00 | 239 | Engr. Station - Contractor | 120 | mh | 21359.491 | 120 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 05 | 05.04.01.00 | 242 | Engr. P&C - Eversource | 80 | mh | 5439.1246 | 80 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 05 | 05.04.02.00 | 243 | Engr. P&C - Contractor | 160 | mh | 28832.217 | 160 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 05 | 05.07.01.00 | 247 | Engr. SS Drafting/Project Services - Eversource | 40 | mh | 2817.0942 | 40 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 06 | 06.04.02.00 | 480 | Miscellaneous Cabinet/ Devices Panel Plate Repacments, (Furnish) | 8 | ea | 6371.4181 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 06 | 06.04.02.00 | 478 | Relays AAB FT-1 9R Test Device, (Furnish) | 40 | ea | 29202.3327 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 06 | 06.04.02.00 | 470 | Relays SEL-351S (Transformer and Feeder Protection), (Furnish) | 8 | ea | 40639.0281 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 06 | 06.04.02.00 | 476 | Relays SEL-735 (Transformer Protection), (Furnish) | 4 | ea | 16932.9284 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 06 | 06.04.02.00 | 472 | Relays SEL-751 (Transformer and Feeder Protection), (Furnish) | 8 | ea | 33865.8568 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 06 | 06.04.03.00 | 488 | Insulated Control Cable Cable, Control, #12 SIS Switchbourd cable , (Furnish) | 200 | lf | 124.7736 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 06 | 06.04.03.00 | 486 | Insulated Control Cable Cable, Control, #14 SIS Switchbourd cable , (Furnish) | 200 | lf | 57.0773 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 06 | 06.04.03.00 | 482 | Insulated Control Cable Cable, Control, Lug, Termination #12-10 AWG , (Furnish) | 100 | ea | 94.2439 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 06 | 06.04.03.00 | 484 | Insulated Control Cable Cable, Control, Lug, Termination #18-14 AWG, (Furnish) | 100 | ea | 70.3511 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 06 | 06.04.03.00 | 298 | Insulated Control Cable Cable, Control, User Defined, (Furnish) | 10000 | lf | 19578.8367 | 0 | Length per Estimator | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.01.02.01 | 132 | Switching & Tagging (Internal labor) | 320 | mh | 21146.7075 | 320 | 20 ops x 8 hrs/ops x 2 switchers | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.01.04.00 | 0 | Demobilization | 1 | ls | 33081.5768 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.01.04.00 | 0 | Mobilization | 1 | ls | 33081.5768 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.03.02.12 | 489 | Insulated Control Cable Cable, Control, #12 SIS Switchbourd cable , (Install) | 200 | lf | 230.7988 | 1.2 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.03.02.12 | 487 | Insulated Control Cable Cable, Control, #14 SIS Switchbourd cable , (Install) | 200 | lf | 192.3306 | 1 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.03.02.12 | 483 | Insulated Control Cable Cable, Control, Lug, Termination #12-10 AWG , (Install) | 100 | ea | 2307.9667 | 12 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.03.02.12 | 485 | Insulated Control Cable Cable, Control, Lug, Termination #18-14 AWG, (Install) | 100 | ea | 1538.6445 | 8 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.03.02.12 | 299 | Insulated Control Cable Cable, Control, User Defined, (Install) | 10000 | lf | 46159.3346 | 240 | Length per Estimator | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.03.03.02 | 481 | Miscellaneous Cabinet/ Devices Panel Plate Repacments, (Install) | 8 | ea | 1538.6445 | 8 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.03.03.02 | 479 | Relays AAB FT-1 9R Test Device, (Install) | 40 | ea | 19233.0561 | 100 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.03.03.02 | 471 | Relays SEL-351S (Transformer and Feeder Protection), (Install) | 8 | ea | 492366.2362 | 2560 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.03.03.02 | 477 | Relays SEL-735 (Transformer Protection), (Install) | 4 | ea | 246183.1181 | 1280 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 07 | 07.03.03.02 | 473 | Relays SEL-751 (Transformer and Feeder Protection), (Install) | 8 | ea | 492366.2362 | 2560 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 08 | 08.01.02.00 | 138 | Lead Commissioning Engr. (LCE), Contractor | 2600 | mh | 663104.936 | 2600 | 50% mhrs of Field Test Engr. | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 08 | 08.02.02.00 | 140 | Field Test Engr., Contractor | 5200 | mh | 1151386.2828 | 5200 | SEL-751 8 reloays x 300 mhrs per RRA = 2,400 mhrs SEL-735 4 reloays x 300 mhrs per RRA = 1,200 mhrs SEL-351S 8 reloays x 420 mhrs per RRA = 3,360 mhrs Total = 6,920 mhrs x 75% efficiency = 5,200 mhrs | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 09 | 09.01.02.00 | 148 | Project Manager, Contractor | 138 | mh | 25029.7922 | 138 | 4 mns x 4.3 wks/mn x 8 mhrs/wk | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 09 | 09.03.01.00 | 149 | Purchasing, Eversource | 24 | mh | 1790.1008 | 24 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 09 | 09.04.01.00 | 167 | System Planning, Eversource | 40 | mh | 3104.7161 | 40 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 09 | 09.08.01.00 | 159 | Estimating, Eversource | 40 | mh | 2705.7181 | 40 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 09 | 09.09.01.00 | 157 | Project Controls, Project Performance, Eversource | 24 | mh | 1278.1306 | 24 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 09 | 09.09.01.00 | 155 | Project Controls, Scheduling, Eversource | 24 | mh | 1278.1306 | 24 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 09 | 09.10.01.00 | 161 | Asset Management, Eversource | 40 | mh | 2568.9001 | 40 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 09 | 09.11.01.00 | 452 | Construction Manager (CR), Eversource | 344 | mh | 59170.1898 | 344 | 2mns x 4.3wks/mn x 40 mhrs/wk | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 10 | 10.01.00.00 | 475 | Removals - Station - ABB-REF610 Relays (Labor) | 8 | ea | 49236.6236 | 256 | 10% of install (320 mhrs) | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 10 | 10.01.00.00 | 474 | Removals - Station - SEL-551 Relays (Labor) | 8 | ea | 49236.6236 | 256 | 10% of install (320 mhrs) | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 10 | 10.01.00.00 | 491 | Removals - Station - Test Switches (Labor) | 40 | ea | 9616.5281 | 50 | 50% of install (2.5 mhrs) | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 10 | 10.01.00.00 | 492 | Removals - Station - Wiring (Labor) | 1 | ea | 15386.4449 | 80 | 2 elec x 1 wk x 40 mhrs/wk | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 11 | 11.00.00.03 | 0 | CWIPDistribution | 1 | ls | 76400.0733 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 12 | 12.07.00.00 | 455 | Risk - Construction - Design / Scope changes | 1 | ls | 200000 | 0 | Change orders, increase labor and materials costs. | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 12 | 12.07.00.00 | 461 | Risk - Construction - Labor costs impact | 1 | ls | 220000 | 0 | Salaries increase yearly or a labor shortage of qualified personnel. Possible overtime. | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 12 | 12.07.00.00 | 460 | Risk - Construction - Mat'l costs impact | 1 | ls | 300000 | 0 | Material costs increase especially precious metals and possible tariffs. | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 12 | 12.07.00.00 | 454 | Risk - Construction - Weather delays imact | 1 | ls | 50000 | 0 | Delay in schedule due to adverse weather. | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 13 | 13.01.00.00 | 0 | Indirect - Non-Productive Basis | 1 | ls | 55403.688 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 13 | 13.02.00.00 | 0 | Indirect - Payroll Benefit Basis | 1 | ls | 26548.6774 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 13 | 13.03.00.00 | 0 | Indirect - Gen Svc Co OH Basis | 1 | ls | 10600.505 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 13 | 13.05.00.00 | 0 | Indirect - E&S Station Basis | 1 | ls | 1458437.1688 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 13 | 13.06.00.00 | 0 | Indirect - AS & E Basis | 1 | ls | 58085.0383 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 13 | 13.08.00.00 | 0 | Indirect - Lobby Stock Basis | 1 | ls | 0 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 13 | 13.09.00.00 | 0 | Indirect - MDEC Basis | 1 | ls | 248747.8036 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 13 | 13.10.00.00 | 0 | Indirect - Vehicles OH Basis | 1 | ls | 64151.6387 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 14 | 14.01.00.00 | 0 | AFUDC | 1 | ls | 333060.4886 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 496 - Rev 2 | 15 | 15.15.00.00 | 217 | Contingency - General | 1 | ls | 331723 | 0 |  | F. Station 496 feeder protection upgrades (interconnection) | F
Hyde Park BESS - Sta. 360 - Rev 3 | 01 | 01.04.00.00 | 85 | Contractor ROW, Easment Costs | 1 | ls | 2532 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 01 | 01.04.00.00 | 84 | Land Costs | 1 | ls | 578.37 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 02 | 02.01.00.00 | 93 | Enviromental, Eversource | 160 | mh | 9793.5143 | 160 | Mhrs from E-23-373 estimate | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 02 | 02.02.00.00 | 346 | City/Municipal Permits (Zoning, Building, etc.) | 40 | ea | 7096.726 | 40 | Zoning relief and permits. City of Boston Article 80 & zoning variance. | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 02 | 02.02.00.00 | 345 | DEP Listed Site - Wast Management | 40 | ea | 7096.726 | 40 | Permit needed for authorization to construct on closed landfill facility. | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 02 | 02.02.00.00 | 350 | eNOI, EPA 2022, Submittal | 24 | ea | 4258.0356 | 24 | Disturb greater than 1 acre of land. | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 02 | 02.02.00.00 | 94 | Environmental, Contractor | 160 | mh | 28386.9039 | 160 | Mhrs from E-23-373 estimate | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 02 | 02.02.00.00 | 348 | Mass DEP | 24 | ea | 4258.0356 | 24 | Tier II reporting for batteries. | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 02 | 02.02.00.00 | 347 | Soil Sampling/Disposal | 120 | ea | 23141.0742 | 120 | Samples plus soil management plan needed. | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 02 | 02.02.00.00 | 349 | Storm Water Pollution Prevention Plan (SWPPP) | 80 | ea | 14193.4519 | 80 | Develop plan and inspections are required. | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 02 | 02.03.01.00 | 88 | Legal, Environmental, Eversource | 1 | ls | 70700.04 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 02 | 02.05.00.00 | 92 | Fees - Environmental Permits - Contractor | 1 | ls | 10302.56 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 03 | 03.01.00.00 | 201 | Project Services (Outreach), Eversource (Actuals input) | 1 | ls | 81346.44 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 03 | 03.01.00.00 | 203 | Project Services (Outreach), Eversource (Manual input) | 480 | mh | 29380.5429 | 480 |  | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 03 | 03.01.00.00 | 0 | SCS, Internal, Traditional | 1 | ls | 36676.0522 | 0 |  | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 03 | 03.02.00.00 | 202 | Project Services (Outreach), Contractor (Actuals input) | 1 | ls | 3454.72 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 03 | 03.02.00.00 | 204 | Project Services (Outreach), Contractor (Manual input) | 480 | mh | 85160.7116 | 480 |  | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 03 | 03.02.00.00 | 0 | SCS, External, Traditional | 1 | ls | 55014.0784 | 0 |  | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 04 | 04.01.00.00 | 197 | Siting, Eversource (Actuals input) | 1 | ls | 68307.72 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 04 | 04.01.00.00 | 193 | Siting, Eversource (Manual input) | 180 | mh | 11656.9934 | 180 | Neighborhood is concerned about losing land and visual concerns near shopping plaza. Screening/buffering likely for abutting residential neighborhood. Increase traffic concerns. | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 04 | 04.01.00.00 | 0 | Siting, Internal, Application | 1 | ls | 116904.9165 | 0 |  | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 04 | 04.02.00.00 | 198 | Siting, Contractor (Actuals input) | 1 | ls | 6595 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 04 | 04.02.00.00 | 0 | Siting, External, Application | 1 | ls | 1052144.2485 | 0 |  | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.01.01.00 | 106 | Engr. Civil - Eversource - station | 80 | mh | 5634.1885 | 80 | Costs per email dated 9/18/26, Eng. Costs total $501,000 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.01.02.00 | 107 | Engr. Civil - Contractor - station | 80 | mh | 14151.4368 | 80 | Costs per email dated 9/18/26, Eng. Costs total $501,000 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.01.02.00 | 437 | Engr. Civil - Contractor - station | 1 | ls | 32190.27 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.02.01.00 | 238 | Engr. Station - Eversource | 360 | mh | 24476.0609 | 360 | Costs per email dated 9/18/26, Eng. Costs total $501,000 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.02.01.00 | 439 | Engr. Station - Eversource | 1 | ls | 129726.39 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.02.02.00 | 239 | Engr. Station - Contractor | 1050 | mh | 186895.5466 | 1050 | Costs per email dated 9/18/26, Eng. Costs total $501,000 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.02.02.00 | 440 | Engr. Station - Contractor | 1 | ls | 24652.8 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.03.01.00 | 442 | Engr. Lines D AG - Eversource | 1 | ls | 127849.97 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.04.01.00 | 242 | Engr. P&C - Eversource | 440 | mh | 29915.1855 | 440 | Costs per email dated 9/18/26, Eng. Costs total $501,000 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.04.01.00 | 443 | Engr. P&C - Eversource | 1 | ls | 69427.64 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.04.02.00 | 243 | Engr. P&C - Contractor | 900 | mh | 162181.2205 | 900 | Costs per email dated 9/18/26, Eng. Costs total $501,000 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.05.01.00 | 126 | Engr. SCADA - Eversource | 120 | mh | 8729.3094 | 120 | Mhrs from E-23-373 estimate | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.05.02.00 | 127 | Engr. SCADA - Contractor | 160 | mh | 28479.3214 | 160 | Mhrs from E-23-373 estimate SCADA Settings and layout | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.06.01.00 | 128 | Engr. Telecom - Eversource | 80 | mh | 5819.5396 | 80 | Mhrs from E-23-373 estimate | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.06.01.00 | 444 | Engr. Telecom - Eversource | 1 | ls | 3963.13 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.06.02.00 | 129 | Engr. Telecom - Contractor | 80 | mh | 14239.6607 | 80 | Costs per email dated 9/18/26, Eng. Costs total $501,000 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 05 | 05.07.01.00 | 247 | Engr. SS Drafting/Project Services - Eversource | 380 | mh | 26762.3953 | 380 | Costs per email dated 9/18/26, Eng. Costs total $501,000 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.01.00 | 302 | 38kV Circuit Breakers SIEMENS SD7-1200 Amps, 15kV, (Furnish) | 4 | ea | 1327378.7611 | 0 | Per project team - breaker cost includes, relays, cabinets, DC battery, PTs, hook type switches and skid. Cost per breaker is $300K per project team. | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.05.00 | 326 | Station Service Transformers, Three-Phase, 1,500 kVA, 13.8kV-480V, Pad Mount, (Furnish) | 1 | ea | 87656.7749 | 0 | Maximo #534534, change quantity to one per email dated 9/16/26 | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.05.00 | 338 | Transformer, 13.8kV - 480V, Generator Step-Up (GSU), 3 MVA, Pad Mount, (Furnish) | 4 | ls | 1066455.918 | 0 | Cost $882,302 Bidder lists dated 7/28/23. Add 3% per year inflation = $964,116/4 es = $241,029 | C. Battery balance-of-plant (GSUs, EMS/comms, aux power) | C
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.08.00 | 421 | Power Cable 3 Phase 15kV EPR Triplex (Furnish) | 500 | lf | 52265.5387 | 0 | Per Estimator - 500LF for each of the SSVT | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.08.00 | 411 | Power Cable 3 Phase 15kV EPR Triplex (Furnish) - 250 MCM | 2750 | lf | 199305.921 | 0 | Riser Structure to GSU | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.08.00 | 423 | Power Cable, 15 kV Elbow Connectors (Furnish) | 27 | ea | 3551.3806 | 0 | for pad mount SSVT (3) plus (4 metering transclosure x 6 ea.) = 27 | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.08.00 | 415 | Power Cable, 250 MCM, 15kV, Terminations (Furnish) | 48 | ea | 7056.8976 | 0 | 12 runs x 6 terminations/run cost on line | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.08.00 | 413 | Power Cable, 600V, 4/O Cable, 1-Conductor, Insulated, (Furnish) - CU | 2000 | lf | 16017.0371 | 0 | GSU to BESS cost on line | B. Battery installation & integration (owner scope) | B
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.08.00 | 417 | Power Cable, 600V, 4/O Cable, Insulated, (Furnish) Length per Estimator 4 cond. AL | 500 | lf | 8268.4635 | 0 | SSVT -1500 kVA Pad Trans and one Dry Type - cost on line Wake Forest Aluminum | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.09.00 | 310 | Switch, Disconnect, 14.4kV, 3 pole/single throw, 1200 amp (includes Insulators and Manual Operating Mechanism), (Furnish) | 8 | ea | 30972.1711 | 0 | Located on breaker skid | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.99.00 | 478 | AC/ DC Distribution Panels, Aux. Power Systems, (Furnish) | 1 | ea | 67724.5126 | 0 | Cost $56,030, Bidder lists dated 7/28/23. Add 3% per year inflation = $61,225 | C. Battery balance-of-plant (GSUs, EMS/comms, aux power) | C
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.99.00 | 419 | Automatic Transfer Switch, 400 amps, 3 Phase, (Furnish) | 2 | ea | 21503.5359 | 0 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.99.00 | 428 | Fuse Cutouts, 15 KV, 1 Phase, (Furnish) | 33 | ea | 8266.4503 | 0 | Cost on line - Per estimator for three SSVTs (9) and PTs (24) Total 33. | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.99.00 | 472 | Insulators - 15kV, Dead-End Insulators, (Furnish) | 12 | ea | 1592.8545 | 0 | OH cable from breaker to wood pole | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.99.00 | 445 | Misc. Eqt & Construction, Material (Furnish) | 1 | ls | 1213042 | 0 | Actual Costs to 9/23/26 | A. Battery supply contract (Nomad) | A
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.02.99.00 | 320 | Wood Poles Distribution Wood Poles - 45ft, (Furnish) | 8 | ea | 21238.0602 | 0 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.03.02.00 | 470 | Cable Single Phase/Bare Cable 556 mcm ACSR, (26/7) Dove, (Furnish) | 250 | lf | 580.7282 | 0 | 25' x 6 conductors x 2 - OH cable from breaker to wood pole on each side of the breaker | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.04.02.00 | 334 | Outdoor Metering Transclosure, , (Furnish) | 4 | ea | 152648.5575 | 0 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.04.03.00 | 298 | Insulated Control Cable Cable, Control, User Defined, (Furnish) | 10000 | lf | 19578.8367 | 0 | Length per Estimator | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.06.00.00 | 476 | Communications, User Defined, (Furnish) | 1 | ea | 263177.1747 | 0 | Cost $217,733, Bidder lists dated 7/28/23. Add 3% per year inflation = $237,922 | C. Battery balance-of-plant (GSUs, EMS/comms, aux power) | C
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.08.00.00 | 393 | 4" Galvanized Rigid Conduit (Furnish) | 480 | lf | 14174.8123 | 0 | 40LF x 12 runs - GSU to Batteries | B. Battery installation & integration (owner scope) | B
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.08.00.00 | 395 | 4" GRC 90 Degree Elbow - 36" Sweep (Furnish) | 24 | ea | 22007.9399 | 0 | 12 runs x 2 sweeps - GSU to Batteries. | B. Battery installation & integration (owner scope) | B
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.08.00.00 | 432 | Batteries, Nomad Batteries Voyager Eagle LFP BESS System , (Furnish) | 1 | ls | 11778061.8259 | 0 | See cover agreement dated 12/6/25 =.$11,860,850 minus actual cost and downpayment $1,213,042.82 total = $10,647,808 | A. Battery supply contract (Nomad) | A
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.08.01.00 | 260 | Grounding Systems, Cable, UG, 4/0 copper, bare, (Furnish) | 4400 | lf | 25600.7117 | 0 | 200'x200' Cost $123,768 Bidder lists dated 7/28/23. Add 3% per year inflation = $135,244 all ground grid material | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.08.01.00 | 268 | Grounding Systems, Grounding, Conn, Compression, Ground 2-4/0, (Furnish) | 25 | ea | 774.3043 | 0 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.08.01.00 | 266 | Grounding Systems, Grounding, Connector, Compression, Ground, C-Tap. , (Furnish) | 50 | ea | 1216.7639 | 0 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.08.01.00 | 264 | Grounding Systems, Grounding, Connector, Compression, Ground, L-Tap. 4/0 cable to 5/8" Rod, (Furnish) | 100 | ea | 2654.7575 | 0 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.08.01.00 | 262 | Grounding Systems, Grounding, Ground Rods "5/8 X 8 FT, (Furnish) | 100 | ea | 2322.9128 | 0 | 20' spacing | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 06 | 06.08.01.00 | 474 | Grounding Systems, Transformers and Grid, (Furnish) | 1 | ls | 116145.6416 | 0 | Cost $123,768 Bidder lists dated 7/28/23. Add 3% per year inflation = $135,244 Minus material only $30,244 of 200'x200' grid total $105,800 | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.01.01.00 | 481 | Fire Suppression (Install) | 1 | ls | 45091.7722 | 0 |  | B. Battery installation & integration (owner scope) | B
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.01.01.00 | 480 | Fire Suppresssion (Furnish) | 1 | ls | 86952.1372 | 0 | Cost $68,640 Bidder lists dated 7/28/23. Add 3% per year inflation = $75,004.78 | B. Battery installation & integration (owner scope) | B
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.01.01.00 | 288 | Roads, Paving - Gravel Driveway - 20 ft. wide, (Furnish) | 760 | lf | 44934.468 | 0 | 20'Wx760' | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.01.01.00 | 289 | Roads, Paving - Gravel Driveway - 20 ft. wide, (Install) | 760 | lf | 274358.2881 | 1900 | 20'Wx760' | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.01.01.00 | 343 | Soil Borings, (Furnish) - Access Rd,. | 24 | ea | 16693.92 | 0 | Per Constructability Review Form | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.01.01.00 | 344 | Soil Borings, (Install) | 24 | ea | 199033.3272 | 1440 |  | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.01.02.01 | 132 | Switching & Tagging (Internal labor) | 32 | mh | 2114.6708 | 32 | 2 ops x 8 hrs/ops x 2 switchers Interconnection to grid switch time | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.01.04.00 | 0 | Demobilization | 1 | ls | 156741.0693 | 0 |  | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.01.04.00 | 0 | Mobilization | 1 | ls | 156741.0693 | 0 |  | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.02.02.02 | 342 | Soil Borings, (Install) - SS | 12 | ea | 137515.5554 | 720 |  | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.02.03.01 | 321 | Wood Poles Distribution Wood Poles - 45ft, (Install) | 8 | ea | 27307.0568 | 128 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.02.03.02 | 422 | Power Cable 3 Phase 15kV EPR Triplex (Install) | 500 | lf | 19727.0642 | 105 | Per Estimator - 500LF for each of the SSVT | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.02.03.02 | 412 | Power Cable 3 Phase 15kV EPR Triplex (Install) - 250 MCM | 2750 | lf | 108498.8583 | 577.5 | Riser Structure to GSU | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.02.05.02 | 341 | Soil Borings, (Furnish) - SS | 12 | ea | 7651.38 | 0 | Per Constructability Review Form | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.01 | 293 | Backfill - Imported fill, (Install) | 570 | cy | 65015.7182 | 285 |  | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.01 | 292 | Backfill - Imported fill, (Furnish) | 570 | cy | 27753.642 | 0 |  | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.01 | 283 | Sitework, Clear & Grub site, (Install) | 4.25 | ac | 83877.6715 | 425 | Access Road | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.01 | 290 | Soil Disposal - Reusable, (Furnish) | 2520 | cy | 67371.3936 | 0 | Cut 2,520 CY of Material | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.01 | 291 | Soil Disposal - Reusable, (Install) | 2520 | cy | 388267.7576 | 2520 | Cut 2,520 CY of Material | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.01 | 286 | Surfacing, Trap Rock 3/4" - Spread to a depth of 6 Inches (Furnish) - SS Gravel | 4900 | sy | 340834.2 | 0 | 210'x210'=44,100SFT/9 = 4,900sy | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.01 | 287 | Surfacing, Trap Rock 3/4" - Spread to a depth of 6 Inches (Install) - SS Gravel | 4900 | sy | 150993.0169 | 980 | 210'x210'=44,100SFT/9 = 4,900sy | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.02 | 270 | Fencing, Chain Link Fencing, (Furnish) | 800 | lf | 18493.2064 | 0 |  | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.02 | 271 | Fencing, Chain Link Fencing, (Install) | 800 | lf | 73955.7634 | 480 |  | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.02 | 276 | Fencing, Gate, manual, (Furnish) | 3 | ea | 3419.935 | 0 | Personnel Gate | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.02 | 277 | Fencing, Gate, manual, (Install) | 3 | ea | 6779.2783 | 44 | Personnel Gate | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.02 | 278 | Retaining wall, Formed and poured walls - 14' Tall (Furnish) | 280 | lf | 109066.944 | 0 |  | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.02 | 279 | Retaining wall, Formed and poured walls - 14' Tall (Install) | 280 | lf | 361286.5245 | 2240 |  | E. Site development & civil (former landfill site) | E
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 336 | Foundation, 3 MVA Transformer 6.6 CY (Furnish) - GSU | 4 | ea | 10864.9596 | 0 | Generator Step Up Transformer | C. Battery balance-of-plant (GSUs, EMS/comms, aux power) | C
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 337 | Foundation, 3 MVA Transformer 6.6 CY (Install) - GSU | 4 | ea | 45852.5754 | 297.6 | Generator Step Up Transformer | C. Battery balance-of-plant (GSUs, EMS/comms, aux power) | C
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 430 | Foundation, D station, 251"x108" Pads for Nomad Batteries, (Furnish) | 12 | ea | 109331.2644 | 0 |  | B. Battery installation & integration (owner scope) | B
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 431 | Foundation, D station, 251"x108" Pads for Nomad Batteries, (Install) | 12 | ea | 231111.7605 | 1500 |  | B. Battery installation & integration (owner scope) | B
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 388 | Foundation, D station, Conrol/SCADA Outdoor Cabinets., (Install) | 1 | ea | 14174.8546 | 92 | 27.25'(W) x 150" (L) | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 387 | Foundation, D station, Control/SCADA Oudoor Cabinets (Furnish) | 1 | ea | 3593.83 | 0 | 27.25'(W) x 150" (L) | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 391 | Foundation, D station, Transclosure, (Furnish) | 4 | ea | 5564.64 | 0 | Metering | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 392 | Foundation, D station, Transclosure, (Install) | 4 | ea | 14791.1527 | 96 | Metering | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 313 | Foundation,15 KV Outdoor 6.81 CY C.B. (Install) | 4 | ea | 7395.5763 | 48 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 312 | Foundation,15 KV Outdoor C.B. 6.81 CY (Furnish) | 4 | ea | 11210.6629 | 0 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 324 | Foundation,15 KV SSVT Pad 4.67 CY (Furnish) | 1 | ea | 1921.9455 | 0 | 1,500 kVA Pad | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.01.03 | 325 | Foundation,15 KV SSVT Pad 4.67 CY (Install) | 1 | ea | 1540.7451 | 10 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.01 | 303 | 38kV Circuit Breakers SIEMENS SD7-1200 Amps, 15kV, (Install) | 4 | ea | 169250.8937 | 880 | Per project team - breaker cost includes, relays, cabinets, DC battery, PTs, hook type switches and skid. Cost per breaker is $300K per project team. | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.04 | 311 | Switch, Disconnect, 14.4kV, 3 pole/single throw, 1200 amp (includes Insulators and Manual Operating Mechanism), (Install) | 8 | ea | 207526.4682 | 1040 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.07 | 327 | Station Service Transformers, Three-Phase, 1,500 kVA, 13.8kV-480V, Pad Mount, (Install) | 1 | ea | 6923.9002 | 36 | Maximo #534534, change quantity to one per email dated 9/16/26 | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.07 | 339 | Transformer, 13.8kV - 480V, Generator Step-Up (GSU), 3 MVA, Pad Mount, (Install) | 4 | ea | 317168.7858 | 1800 |  | C. Battery balance-of-plant (GSUs, EMS/comms, aux power) | C
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.09 | 403 | (1) 4" PVC Conduit Conc. Enc, (Furnish) - Length per Estimator | 300 | lf | 3972.4574 | 0 | Telecommunication | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.09 | 404 | (1) 4" PVC Conduit Conc. Enc, (Install) - Length per Estimator | 300 | lf | 4401.759 | 28.569 | Telecommunication | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.09 | 397 | Ductbank 2x2 Duct - w/excav & backfill, w/o cable, (Furnish) | 440 | lf | 22770.5069 | 0 | 220 'x4 runs - Riser poles to GSU | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.09 | 399 | Ductbank 2x2 Duct - w/excav & backfill, w/o cable, (Furnish) - Length per Estimator | 800 | lf | 41400.9216 | 0 | 200 'x4 runs - Riser poles to Feeder Connections Manholes | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.09 | 398 | Ductbank 2x2 Duct - w/excav & backfill, w/o cable, (Install) | 440 | lf | 103045.026 | 668.8 | 220 'x4 runs - Riser poles to GSU | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.09 | 400 | Ductbank 2x2 Duct - w/excav & backfill, w/o cable, (Install) - Length per Estimator | 800 | lf | 187354.6005 | 1216 | 200 'x4 runs - Riser poles to Feeder Connections Manholes | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.10 | 394 | 4" Galvanized Rigid Conduit (Install) | 480 | lf | 68470.6941 | 216 | 40LF x 12 runs - GSU to Batteries | B. Battery installation & integration (owner scope) | B
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.10 | 396 | 4" GRC 90 Degree Elbow - 36" Sweep (Install) | 24 | ea | 13847.8004 | 72 | 12 runs x 2 sweeps - GSU to Batteries | B. Battery installation & integration (owner scope) | B
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.11 | 485 | Batteries, Nomad Batteries Voyager Eagle LFP BESS System , (Install) | 2 | ea | 1068769.3849 | 5556.94 | Cost from E-23-373 estimate = 16,801 mhrs x 25% = 4,200 mhrs | B. Battery installation & integration (owner scope) | B
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 471 | Cable Single Phase/Bare Cable 556 mcm ACSR, (26/7) Dove, (Install) | 250 | lf | 3990.8936 | 20 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 261 | Grounding Systems, Cable, UG, 4/0 copper, bare, (Install) | 4400 | lf | 42312.7234 | 220 | 200'x200' | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 269 | Grounding Systems, Grounding, Conn, Compression, Ground 2-4/0, (Install) | 25 | ea | 4808.264 | 25 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 267 | Grounding Systems, Grounding, Connector, Compression, Ground, C-Tap. , (Install) | 50 | ea | 9616.5281 | 50 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 265 | Grounding Systems, Grounding, Connector, Compression, Ground, L-Tap. 4/0 cable to 5/8" Rod, (Install) | 100 | ea | 19233.0561 | 100 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 263 | Grounding Systems, Grounding, Ground Rods "5/8 X 8 FT, (Install) | 100 | ea | 19233.0561 | 100 | 20' spacing | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 475 | Grounding Systems, Transformers and Grid, (Install) | 1 | ls | 92318.6693 | 480 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 299 | Insulated Control Cable Cable, Control, User Defined, (Install) | 10000 | lf | 46159.3346 | 240 | Length per Estimator | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 425 | Power Cable, 15 kV Elbow Connectors (Install) | 27 | ea | 20725.8697 | 108 | for pad mount SSVT (3) plus (4 metering transclosure x 6 ea.) = 27 | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 416 | Power Cable, 250 MCM, 15 kV, Terminations (Install) | 48 | ea | 36845.9906 | 192 | 12 runs x 6 terminations/run | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 418 | Power Cable, 600V, 4/O Cable, Insulated, (Install) Length per Estimator 4 cond. AL | 500 | lf | 20150.1511 | 105 | SSVT -1500 kVA Pad Trans - cost on line Wake Forest Aluminum | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.12 | 414 | Power Cable, 600V, 4/O, Cable, 1-Conductor, Insulated, (Install) - CU | 2000 | lf | 57571.8603 | 300 | GSU to BESS | B. Battery installation & integration (owner scope) | B
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.99 | 479 | AC/ DC Distribution Panels, Aux. Power Systesms, (Install) | 1 | ea | 69239.002 | 360 |  | C. Battery balance-of-plant (GSUs, EMS/comms, aux power) | C
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.99 | 420 | Automatic Transfer Switch, 400 amps, 3 Phase, (Install) | 2 | ea | 6923.9002 | 36 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.99 | 429 | Fuse Cutouts, 15 KV, 1 Phase, (Install) | 33 | ea | 12693.817 | 66 | Cost on line - Per estimator for three SSVTs (9) and PTs (24) Total 33. | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.99 | 473 | Insulators - 15kV, Dead-End Insulators, (Install) | 12 | ea | 13847.8004 | 72 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.99 | 487 | Misc. Eqt - Line Construction, (Install) - OH Tower, Wire Stringing | 1 | ls | 25659.85 | 0 | Actual Costs to 9/23/26 | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.99 | 294 | Switchyard Lighting (Freestanding pole Mnt), Area Light 100 HPS Yard Luminare Complete DTR21.361.0A (Furnish) | 12 | ea | 17389.5 | 0 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.99 | 295 | Switchyard Lighting (Freestanding pole Mnt), Area Light 100 HPS Yard Luminare Complete DTR21.361.0A (Install) | 12 | ea | 14367.217 | 72 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.99 | 297 | Switchyard Lighting (Freestanding pole Mnt), Elect Hook Up - Assume 100 ft direct bury XLP Cable between lights and to CB Panel (Install) | 1200 | lf | 239453.6172 | 1200 | Elect Hook Up - Assume 100 ft direct bury XLP Cable between lights and back to CB Panel | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.02.99 | 296 | Switchyard Lighting (Freestanding pole Mnt), Elect Hook Up - Assume 100 ft direct bury XLP Cable between lights and to CB Panel (Furnish) | 1200 | lf | 41734.8 | 0 | Elect Hook Up - Assume 100 ft direct bury XLP Cable between lights and back to CB Panel | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.03.02 | 335 | Outdoor Metering Transclosure , (Install) | 4 | ea | 92318.6693 | 480 |  | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.03.03.03 | 477 | Communications, User Defined, (Install) | 1 | ea | 92318.6693 | 480 |  | C. Battery balance-of-plant (GSUs, EMS/comms, aux power) | C
Hyde Park BESS - Sta. 360 - Rev 3 | 07 | 07.09.00.00 | 352 | Traffic Control, substation constr., (Furnish) | 1 | ls | 11593 | 0 | Increase traffic during construction. | D. Station 360 13.8 kV switching & interconnection facilities | D
Hyde Park BESS - Sta. 360 - Rev 3 | 08 | 08.01.02.00 | 138 | Lead Commissioning Engr. (LCE), Contractor | 1600 | mh | 408064.576 | 1600 | 50% mhrs of Field Test Engr. | G. Testing & commissioning | G
Hyde Park BESS - Sta. 360 - Rev 3 | 08 | 08.02.02.00 | 140 | Field Test Engr., Contractor | 3200 | mh | 708545.4048 | 3200 | Mhrs from E-23-373 estimate | G. Testing & commissioning | G
Hyde Park BESS - Sta. 360 - Rev 3 | 08 | 08.03.01.00 | 141 | Field Communications (SCADA), Eversource | 1650 | mh | 119733.174 | 1650 | Mhrs from E-23-373 estimate | G. Testing & commissioning | G
Hyde Park BESS - Sta. 360 - Rev 3 | 08 | 08.04.02.00 | 144 | Field Telecom, Contractor | 120 | mh | 26570.4527 | 120 | Per Estimator | G. Testing & commissioning | G
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.01.01.00 | 147 | Project Manager - Eversource | 1278 | mh | 92286.8554 | 1278 | 3 days per construction week and 8 hours per week for lead up year plus 40 mhrs close out. Const: 10 mns x 4.3wks/mn x 24 hrs/wk = 1,032 Up to const: 6 mns x 4.3wks/mn x 8 hrs/wk = 206 40 hrs close out Total 1,278 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.01.01.00 | 446 | Project Manager - Eversource | 1 | ls | 413557.18 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.01.02.00 | 148 | Project Manager, Contractor | 2172 | mh | 393947.1648 | 2172 | 5 days per construction week and 16 hours per week for lead up year plus 40 mhrs close out. Const: 10 mns x 4.3wks/mn x 40 hrs/wk = 1,720 Up to const: 6 mns x 4.3wks/mn x 16 hrs/wk = 412 40 hrs close out Total 2,172 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.01.02.00 | 447 | Project Manager, Contractor | 1 | ls | 207014.17 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.02.01.00 | 153 | Project Controls, IP, Eversource | 120 | mh | 6352.4927 | 120 | Mhrs from E-23-373 estimate | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.03.01.00 | 151 | Contracts, Eversource | 120 | mh | 8950.5041 | 120 | Mhrs from E-23-373 estimate | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.03.01.00 | 149 | Purchasing, Eversource | 40 | mh | 2983.5014 | 40 |  | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.04.01.00 | 167 | System Planning, Eversource | 40 | mh | 3104.7161 | 40 | Mhrs from E-23-373 estimate | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.04.01.00 | 448 | System Planning, Eversource | 1 | ls | 53528.66 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.08.01.00 | 159 | Estimating, Eversource | 40 | mh | 2705.7181 | 40 | Per estimator | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.08.01.00 | 449 | Estimating, Eversource | 1 | ls | 10113 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.08.02.00 | 160 | Estimating, Contractor | 40 | mh | 7096.726 | 40 | per estimator | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.09.01.00 | 157 | Project Controls, Project Performance, Eversource | 480 | mh | 25562.6111 | 480 |  | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.09.01.00 | 488 | Project Controls, Project Performance, Eversource | 1 | ls | 9913.77 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.09.01.00 | 155 | Project Controls, Scheduling, Eversource | 80 | mh | 4260.4352 | 80 |  | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.09.02.00 | 491 | Project Management, (PM/)APM, Contractor | 1 | ls | 188728.56 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.10.01.00 | 161 | Asset Management, Eversource | 40 | mh | 2568.9001 | 40 | Mhrs from E-23-373 estimate | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.11.01.00 | 253 | Construction Manager (CR), Eversource | 1 | ls | 89381.98 | 0 | Actual Costs to 9/23/26 | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.11.01.00 | 452 | Construction Manager (CR), Eversource | 1548 | mh | 266265.854 | 1548 | 9mns x 4.3wks/mn x 40 mhrs/wk | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 09 | 09.12.01.00 | 175 | Vegetation Mgmt., Eversource | 120 | mh | 7970.7539 | 120 |  | H. Owner soft costs (engineering, siting, environmental, outreach, PM, land) | H
Hyde Park BESS - Sta. 360 - Rev 3 | 11 | 11.00.00.01 | 0 | Indirect - SUT-Material-External | 1 | ls | 58459.3147 | 0 |  | I. Taxes, CWIP, builders-risk insurance | I
Hyde Park BESS - Sta. 360 - Rev 3 | 11 | 11.00.00.02 | 170 | Tax - Property | 1 | ls | 38348.41 | 0 | actual input row | I. Taxes, CWIP, builders-risk insurance | I
Hyde Park BESS - Sta. 360 - Rev 3 | 11 | 11.00.00.03 | 0 | CWIPDistribution | 1 | ls | 525183.9021 | 0 |  | I. Taxes, CWIP, builders-risk insurance | I
Hyde Park BESS - Sta. 360 - Rev 3 | 11 | 11.01.00.04 | 483 | BAR Insurance | 1 | ls | 165541.5856 | 0 | Bar Insurance (Builders all risk coverage), over $50M, for stations 0.7% and Lines 1.5%, of Material, Labor and Equipment. Risk item BAR Deductibles between $250K and $500K. $21,327,866 x 0.7% = $$149,295 | I. Taxes, CWIP, builders-risk insurance | I
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.02.00.00 | 457 | Risk - Environmental | 1 | ls | 300000 | 0 | Additional requirements and communication with DEP and review of landfill closure documents. | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.03.00.00 | 456 | Risk - Additional Outreach | 1 | ls | 250000 | 0 | Increase costs for outreach services which can cause delays in schedule. | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.05.00.00 | 464 | Risk - Engineering - Elec. - P&C | 1 | ls | 300000 | 0 | Increase P&C engineering costs due to design changes and failed test results. | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.05.00.00 | 463 | Risk - Engineering - Elec. - Station | 1 | ls | 300000 | 0 | Increase engineering costs due to design changes and change orders. | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.07.00.00 | 484 | Risk - Construction - Bar Insurance | 1 | ls | 250000 | 0 | Bar Insurance deductibles | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.07.00.00 | 455 | Risk - Construction - Design / Scope changes | 1 | ls | 800000 | 0 | Change orders, increase labor and materials costs. | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.07.00.00 | 461 | Risk - Construction - Labor costs impact | 1 | ls | 800000 | 0 | Salaries increase yearly or a labor shortage of qualified personnel. Possible overtime. | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.07.00.00 | 460 | Risk - Construction - Mat'l costs impact | 1 | ls | 1000000 | 0 | Material costs increase especially precious metals and possible tariffs. | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.07.00.00 | 453 | Risk - Construction - Potential UG Obstructions | 1 | ls | 450000 | 0 | Unforeseen UG facilities not shown on drawings that must be removed or relocated. | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.07.00.00 | 462 | Risk - Construction - Siting / Permiting Impacts | 1 | ls | 250000 | 0 | Delay in schedule, increase labor costs due to delays in receiving permits. | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.07.00.00 | 458 | Risk - Construction - Soil contamination impact | 1 | ls | 300000 | 0 | Unexpected remediation needed. | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 12 | 12.07.00.00 | 454 | Risk - Construction - Weather delays imact | 1 | ls | 300000 | 0 | Delay in schedule due to adverse weather. | J. Risk register | J
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.01.00.00 | 0 | Indirect - Non-Productive Basis | 1 | ls | 383032.4694 | 0 |  | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.01.00.00 | 205 | Indirects - Non-Productive Time (ZNP) | 1 | ls | 184571.23 | 0 | actual input row | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.02.00.00 | 0 | Indirect - Payroll Benefit Basis | 1 | ls | 172916.8609 | 0 |  | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.02.00.00 | 206 | Indirects - Payroll Benefits (ZPB) | 1 | ls | 6753.86 | 0 | actual input row | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.03.00.00 | 0 | Indirect - Gen Svc Co OH Basis | 1 | ls | 166272.4518 | 0 |  | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.03.00.00 | 207 | Indirects - General Services OH (ZGS) | 1 | ls | 743486.83 | 0 | actual input row | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.05.00.00 | 0 | Indirect - E&S Station Basis | 1 | ls | 3956889.9875 | 0 |  | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.05.00.00 | 209 | Indirects - E&S Stations | 1 | ls | 828937.32 | 0 | actual input row | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.06.00.00 | 0 | Indirect - AS & E Basis | 1 | ls | 335913.4654 | 0 |  | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.06.00.00 | 210 | Indirects - AS&E (ZAS) | 1 | ls | 33204.45 | 0 | actual input row | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.08.00.00 | 0 | Indirect - Lobby Stock Basis | 1 | ls | 0 | 0 |  | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.08.00.00 | 212 | Indirects - Lobby Stock | 1 | ls | 69243.95 | 0 | actual input row | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.09.00.00 | 0 | Indirect - MDEC Basis | 1 | ls | 641900.2231 | 0 |  | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.09.00.00 | 213 | Indirects - MDEC (ZMI) | 1 | ls | 95912.21 | 0 | actual input row | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.10.00.00 | 0 | Indirect - Vehicles OH Basis | 1 | ls | 443511.2804 | 0 |  | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 13 | 13.10.00.00 | 214 | Indirects - Vehicles | 1 | ls | 2125.77 | 0 | actual input row | L. Indirects / overheads | L
Hyde Park BESS - Sta. 360 - Rev 3 | 14 | 14.01.00.00 | 174 | AFUDC | 1 | ls | 4680899.1944 | 0 | actual input row | M. AFUDC | M
Hyde Park BESS - Sta. 360 - Rev 3 | 15 | 15.15.00.00 | 217 | Contingency - General | 1 | ls | 2283517 | 0 |  | K. Contingency | K
[6 empty] | Total | 57247543.9342